Conventional 4 Zone Fire Alarm Control Panel

The vendor shall provide one completely electrically supervised conventional fire alarm control panel such as the Silent Knight Model SK-4, Fire Lite MS-4, or equal. The system shall contain a fire alarm control panel capable of operating and supervising smoke detection devices, alarm notification devices, and an onboard annunciator. It shall be compatible with System Sensor I3 detectors and System Sensor BEAM 1224 beam type smoke detectors.

The fire alarm control panel shall have a power limited supply, four Class B initiation circuits which shall accommodate heat detectors, smoke detectors, and manual pull stations. Smoke detection shall be achieved with either 2- or 4-wire detectors that are compatible with the system. The initiation inputs shall be programmable as verification zones in which detectors are automatically reset one time before signaling an alarm condition.

The FACP shall have two 2.5 amp or 5 amp (with an additional optional standard transformer) programmable notification outputs. It shall have dedicated relays for alarm, trouble, and supervisory. It shall have two power outputs, one resettable and one non-resettable, each rated at 500 mA.

The FACP shall have an on-board annunciator to indicate alarm, supervisory, trouble, and maintenance conditions. The annunciator must include LEDs for AC, GENERAL TROUBLE, ALARM SILENCE, WALK TEST, EARTH FAULT, and LOW BATTERY. The annunciator shall also contain LEDs to annunciate fire alarms, troubles, supervisory, and maintenance by zone. The FACP must be fully operational from the annunciator and include buttons for ACKNOWLEDGE, ALARM, SILENCE, RESET, and WALK TEST. The annunciator must also have separate DISABLE switches for each zone and notification circuit.

(2) The unit will come complete with at least one 7 AH back up battery, two batteries (7Ah each) if space permits, for housing inside the FACP cabinet. Cabinet must be able to be mounted in a semi recessed fashion and include any trim ring accessory necessary.

Conventional Beam Smoke Detector

(1) The vendor shall provide one single ended, reflected-type conventional beam smoke detector such as System Sensor BEAM 1224 or equal. The unit shall have the following specifications and be compatible with the panel listed above:

GENERAL

Range: 16 to 230 Feet

Sensitivity: 25% to 50% Total Obscuration in 6 levels

Level 1 = 25%

Level 2 = 30%

Level 3 = 40%

Level 4 = 50%

Level 5 = 30% to 50% (Acclimate)

Level 6 = 40% to 50% (Acclimate)

Spacing: 30 to 60 Feet (9.1 to 18.3m)

Response Time: ALARM - 20 seconds typical; TROUBLE - 30 seconds typical

Trouble Conditions: Beam Blockage (96% or More Obscuration)

Improper Initial Alignment

Self-compensation limit reached (service needed)

In Alignment mode

Test/Reset Features: Integral Sensitivity Test Filter

Sensitivity Filter (Incremental scale on reflector)

Local Alarm Test Switch

Local Alarm Reset Switch

Remote Test and Reset Switch Capability

Indicators: ALARM - Remote Output, Local LED (red)

TROUBLE - Remote Output, Local LED (yellow), Blink Pattern Indicates Trouble Diagnostics

NORMAL OPERATION - Local LED (flashing green once every 5 sec.)

ALIGNMENT AIDS - Optical Gunsight (coarse adjustment), 00 to 99 Digital Display (fine adjustment)

RELAYS - Alarm; Trouble

SENSITIVITY - Digital Display Readout in Percent Obscuration

ENVIRONMENTAL

Temperature: –22°F to 131°F (–30°C to 55°C)

Humidity: 10% to 93% RH Non-condensing

MECHANICAL

Mounting: Wall only without optional accessories

Wiring: Plug-in Terminal Blocks (12 to 22AWG)

Adjustment Angle: ±10° Horizontal and Vertical

ELECTRICAL

Voltage: 10.2 to 32 VDC

Maximum Ripple Voltage: 6.0 volts (Peak-to-peak); NOTE: ripple must not fall below minimum 	operating voltage specification

Current (24 VDC): Avg. Standby - 17mA Max.

Avg. Alarm - 38.5mA Max.

Avg. Trouble - 8.5mA Max.

Avg. Alignment - 28mA Max.

Current (Test Mode, BEAM1224S only): Peak Test- 500mA Max.

Relay Contacts: 0.5A at 30 VDC

Reset Time: 0.3 Seconds Max.

Start-up Time (after 2 min. reset): 60 sec. Max.

Alarm Verification Time: 5 sec. Max.

Remote Output (Alarm & Trouble): VOLTAGE - 15 to 32 VDC; NOTE: Output voltage same as device input  	voltage

CURRENT - 15mA maximum; 6mA minimum; NOTE: Output current is limited by 2.2K ohm resistor

(2)  The vendor shall include a heater kit for use with the transmitter/ receiver unit for   	      	       	prevention of condensation.