VENDORS WHO DO NOT WISH TO RESPOND TO A BID ARE NOT REQUIRED TO DO SO. HOWEVER, VENDORS NOT RESPONDING AND/OR SUBMITTING A “NO BID” RESPONSE TO THREE CONSECUTIVE BID INVITATIONS FOR THE REQUESTED COMMODITY MAY BE REMOVED FROM THE UNIVERSITY’S BIDDERS LIST.

Please Print or Type

| Company Name: |  |  | Phone: |  |
| --- | --- | --- | --- | --- |
| Address: |  |  |  |  |
|  |  |  | Fax: |  |
| City: |  |  | EMail: |  |
| State: |  |  | Web Site: |  |
| Zip Code: |  |  | Tax ID or SSN: |  |

THIS OFFICIAL BID SHEET MUST BESIGNED AND RECEIVED IN A SEALED ENVELOPE WITH BID NUMBER AND BID OPENING DATE CLEARLY NOTED ON OUTSIDE OF ENVELOPE. BIDS MAY NOT BE FAXED DIRECTLY TO THE UNIVERSITY IN RESPONSE TO THIS INVITATION FOR BID. BID WILL BE ACCEPTED EITHER SIGNED IN INK OR WITH ELECTRONIC OR FACSIMILE SIGNATURE. PLEASE ENCLOSE ONE EXTRA COPY OF SIGNED BID. Name (Type or Print): Title: Signature: Date:

# STANDARD TERMS AND CONDITIONS

| 1. | PREPARATION OF BIDS |  |  |
| --- | --- | --- | --- |
|  | 1.1 | Failure to examine any drawings, specifications, and instructions will be at bidder’s risk. |  |
|  | 1.2 | All prices and notations must be printed in ink or typewritten. No erasures permitted. Errors may be crossed out and corrections printed in ink or typewritten adjacent, and must be initialed in ink by person signing bid. |  |
|  | 1.3 | Brand Name References: Unless specified “No Substitute” any catalog brand name or manufacturer’s reference used in the bid invitation is descriptive only, not restrictive, and used to indicate the type and quality desired. If bidding on other than referenced specifications, the bid must show the manufacturer, brand or trade name, and other descriptions, and should include the manufacturer’s illustrations and complete descriptions of the product offered. The University reserves the right to determine whether a substitute offered is equivalent to and meets the standards of the item specified, and the University may require the bidder to supply additional descriptive material, samples, or demonstrators. The bidder guarantees that the product offered will meet or exceed the referenced product and/or specifications identified in this bid invitation. If the bidder takes no exception to the specifications, bidder will be required to furnish the product exactly as specified in the invitation. |  |
|  | 1.4 | Samples: Samples or demonstrators, when requested, must be furnished free of expense to the University. Samples not destroyed during reasonable examination will become property of the University unless bidder states otherwise. All demonstrators will be returned after reasonable examination. Each sample should be marked with the bidder’s name and address, bid number and item number. |  |
|  | 1.5 | Time of Performance: The number of calendar days in which delivery will be made after receipt of order shall be stated in the bid. |  |
| 2. | SUBMISSION OF BIDS |  |  |
|  | 2.1 | Bids, modifications or corrections thereof received after the closing time specified will not be considered. |  |
| 3. | ACCEPTANCE OF BIDS |  |  |
|  | 3.1 | The University reserves the right to accept or reject all or any part of a bid or any and all bids, to waive any informality, and to award the bid to best serve the interest of the University. |  |
|  | 3.2 | If a bidder fails to state the time within which a bid must be accepted, it is understood and agreed that the University shall have 60 days to accept. |  |
| 4. | ERROR IN BID |  |  |
|  | 4.1 | In case of error in the extension of prices in the bid, the unit price will govern. No bid shall be altered or amended after the specified time for opening bids. |  |
| 5. | AWARD |  |  |
|  | 5.1 | Contracts and purchases will be made or entered into with the lowest responsible bidder meeting specifications or on the basis for best value. |  |
|  | 5.2 | When more than one item is specified in the Invitation, the University reserves the right to determine the low bidder either on the basis of the individual items or on the basis of all items included in its Invitation for Bids, or as expressly stated in the Invitation for Bid. |  |
|  | 5.3 5.4 | A written purchase order or contract award mailed, or otherwise furnished, to the successful bidder within the time of acceptance specified in the Invitation for Bid results in a binding contract without further action by either party. The contract shall not be assignable by the vendor in whole or part without the written consent of the University. Vendors awarded contracts for commodities and/or services are encouraged to participate in our University Shopping Mall. This online catalog database is operated by a third party provider and will allow all University departments to place orders to multiple vendors online. A monthly maintenance fee, to be negotiated between each vendor and the shopping mall data base provider, is required. |  |
| 6. | DELIVERY |  |  |
|  | 6.1 | The Invitation for Bid will show the number of days to place a commodity in the University designated location under normal conditions. If the bidder cannot meet the stated delivery, alternate delivery schedules may become a factor in award. The University has the right to extend delivery if reasons appear valid. |  |
|  | 6.2 | Delivery shall be made during University work hours only, 8:00 a.m. to 4:30 p.m.., unless prior approval for other shipment has been obtained. |  |
|  | 6.3 | Packing memoranda shall be enclosed with each shipment. |  |
| 7. | ACCEPTANCE AND REJECTION |  |  |
|  | 7.1 | Final inspection and acceptance or rejection may be made at delivery destination, but all materials and workmanship shall be subject to inspection and test at all times and places, and when practicable. During manufacture, the right is reserved to reject articles which contain defective material and workmanship. Rejected material shall be removed by and at the expense of the contractor promptly after notification of rejection. Final inspection and acceptance or rejection of the materials or supplies shall be made as promptly as practicable, but failure to inspect and accept or reject materials or supplies shall not impose liability on the University thereof for such materials or supplies as are not in accordance with the specification. In the event necessity requires the use of materials or supplies not conforming to the specification, payment may be made with a proper reduction in price. |  |
| 8. | TAXES AND TRADE DISCOUNTS |  |  |
|  | 8.1 | Do not include state or local sales taxes in bid price. |  |
|  | 8.2 | Trade discounts should be deducted from the unit price and net price should be shown in the bid. |  |
| 9. | DEFAULT |  |  |
|  | 9.1 | Back orders, default in promised delivery, or failure to meet specifications authorize the University to cancel this contract to the defaulting contractor. The contractor must give written notice to the University of the reason and the expected delivery date. |  |
|  | 9.2 | Consistent failure to meet delivery without a valid reason may cause removal from the bidders list or suspension of eligibility for award. |  |
| 10. | WAIVER |  |  |
|  | 10.1 | The University reserves the right to waive any General Condition, Special Condition, or minor specification deviation when considered to be in the best interest of the University, so long as such waiver is not given so as to deliberately favor any single vendor and would have the same effect on all vendors. |  |
| 11. | CANCELLATION |  |  |
|  | 11.1 | Any contract or item award may be canceled for cause by either party by giving 30 days written notice of intent to cancel. Cause for the University to cancel shall include, but is not limited to, cost exceeding current market prices for comparable purchases; request for increase in prices during the period of the contract; or failure to perform to contract conditions. The contractor will be required to honor all purchase orders that were prepared and dated prior to the date of expiration or cancellation if received by the contractor within period of 30 days following the date of expiration or cancellation. Cancellation by the University does not relieve the Contractor of any liability arising out of a default or nonperformance. If a contract is canceled due to a request for increase in prices or failure to perform, that vendor shall be removed from the Qualified Bidders List for a period of 24 months. Cause for the vendor to cancel shall include, but is not limited to the item(s) being discontinued and unavailable from the manufacturer. |  |
| 12. | ADDENDA |  |  |
|  | 12.1 | Addenda modifying plans and/or specifications may be issued if time permits. No addendum will be issued within a period of three(3) working days prior to the time and date set for the bid opening. Should it become necessary to issue an addendum within the three-day period prior to the bid opening, the bid date will be reset giving bidders ample time to answer the addendum. |  |
|  | 12.2 | Only written addenda is part of the bid packet and should be considered. |  |
| 13. | ALTERNATE BIDS |  |  |
|  | 13.1 | Unless specifically requested alternate bids will not be considered. An alternate is considered to be a bid that does not comply with the minimum provisions of the specifications. |  |
| 14. | BID OPENINGS |  |  |
|  | 14.1 | Bid opening will be conducted open to the public. However, they will serve only to open, read and tabulate the bid price on each bid. No discussion will be entered into with any vendor as to the quality or provisions of the specifications and no award will be made either stated or implied at the bid opening. |  |
| 15. | DEBRIS REMOVAL |  |  |
|  | 15.1 | All debris must be removed from the University after installation of said equipment. |  |

ALL BIDS SUBMITTED SHALL BE IN COMPLIANCE WITH THE GENERAL CONDITIONS SET FORTH HEREIN.  THE BID PROCEDURES FOLLOWED BY THIS OFFICE WILL BE IN ACCORDANCE WITH THESE CONDITIONS.  THEREFORE, ALL VENDORS ARE URGED TO READ AND UNDERSTAND THESE CONDITIONS PRIOR TO SUBMITTING A BID.

# Please send 2 copies of your response to this bid.  The extra copy is needed for bid evaluation purposes.  Please do not send bid responses to different bids in the same envelopes.  Thank You!

Bid the following according to minimum specifications:

| # Item | ## Description | Qty |  | Unit Price |  | Total Price |
| --- | --- | --- | --- | --- | --- | --- |

Request for Proposal

Term Contract for the Purchase of Fan Coils

1.1 Description of Proposal

The University of Arkansas seeks Proposals to establish a Term Contract, in compliance with all University Procurement Policies and Arkansas Procurement Law, for the long term procurement of fan coil units to be used for Campus projects and renovations. Quantities of units by type, configuration and CFM ratings are estimates only for the purpose of bidding, which means that we may purchase more or less than estimated during the first year of the contract and during subsequent option years of the contract, annually renewable up to a maximum of six (6) renewal option years.

1.2 Overview

The University estimates replacing at least fifty (50) units during the first year of the contract in varying configurations and capacities. Currently the University has over two thousand fan coils which need replacement with more modern energy efficient equipment. Therefore, the University requires that any and all equipment offered under this RFP shall be new manufactured units that meet or exceed the minimum specification requirements of this Request for Proposal. Submit your products ARI energy rating certification as well as other required product information with your proposal. Failure to submit the required information may be considered as non-responsive and cause your proposal to be disqualified.

This contract will be utilized by Facilities Management to replace fan coil units in Education and General Use Buildings. However, any other department of the University, such as University Housing, at their discretion, may purchase equipment against this contract at the contract pricing. Further the University may assign the purchase of fan coil units to contractors working on University projects. The successful provider shall extend the same pricing to those authorized agents of the University, as if directly purchased by the University under this agreement. The University reserves the right to place orders against this contract in either small or large lots , whichever is in the best interest of the University.

This contract does not include installation by the  successful provider. The University will be responsible for arranging for the removal of the old equipment and installation of the new equipment, by either using Facilities Management personnel or through other contracting arrangements as necessary.

The intent of the University of Arkansas is to award this RFP as All or None.

2. Minimum Fan Coil Unit Equipment Specifications

2.1 The following specifies the minimum general requirements for all types and styles of fan coil units.

For your  RFP to  be considered responsive , each specific specification requirement must be acknowledged on the form, see Section 2.5, as meeting or exceeding the specific definition of the requirement as stated, by marking YES or NO.  Compliance with this section of the RFP shall be executed in the following sequence.

# 2.2 Your product meets or exceeds the minimum  specification requirement, so the appropriate response is “YES”.

### Example: The minimum specification, among other requirements, calls for the Condensate pan to be a minimum 22 gauge chromate coated galvanized steel, with a bonded internal epoxy resin coating.  Your  product is a 20 gauge galvanized steel, with a bonded internal epoxy resin coating. Your product meets or exceeds minimum and is marked “YES”. In this case the evaluation team would conclude that this exceeds the minimum intended requirement and would be considered for award of innovation and quality points.

# 2.3  If, when considering the specific definition of the requirement as presented, you may find that your  product does not meet or exceed the minimum specified requirement, however, optional equipment is available that will allow the unit to meet or exceed the base specification requirement. The valid response to the RFP requires that equipment to be included in the base price of the equipment in Section V. You shall provide a written explanation as to why you believe that your optional equipment meets or exceeds the intended minimum requirement of the specification.

### Example: With the same minimum specification applying, your base product is a 20 gauge galvanized steel, but is not coated. Your product does not meet or exceed minimum specification as stated, , however as an option you offer an epoxy resin / carbon fiber drain pan, so the cost of this option shall be INCLUDED in the base price response in Section V.  Your explanation  points out that carbon fiber is fully corrosion resistant, and is lighter and stronger than steel. In this case the evaluation team would conclude that this well exceeds the minimum intended requirement and will be considered for award of innovation and quality points.

# 2.4 If, when considering the specific definition of the requirement as presented, you find that your  proposed product does not meet or exceed the minimum specified requirement, you must mark the response as “NO”.

# 2.5 Minimum Specifications:

# If the indication is “NO”, meaning it does not explicitly meet or exceed the minimum requirement as stated, Your proposal will not be considered for further evaluation.

## 2.5.1 GENERAL REQUIREMENTS: Fan coil unit shall consist of cabinet, centrifugal fan, cooling coil, and/or heating coil, condensate pan, filter rack, filter, and electrical controls, completely factory assembled, tested and shipped as one piece.

### 2.5.2 Fan coil unit cabinet shall be minimum 18 gauge galvanized steel. Exposed type units shall have baked-on acrylic powder coated finish.

#### a) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.3 Unit shall be internally insulated with minimum 15 mm thick closed cell elastomeric foam insulation, per ASTM C 1534, “Specification for Flexible Polymeric Foam Sheet Insulation Used as a Thermal and Sound Adsorbing Liner for Duct Systems”. Material to have a flame spread index of less than 25, a smoke index of less than 50, be approved for use in air plenums, and meet NFPA 90A, NFPA 90B and UL 181 for erosion , an Antimicrobial Performance Rating of 0 under ASTM G 21.

#### b) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.4 Unit shall be furnished with a 20 A fused on/off service switch mounted to the unit.

#### c) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.5 Electrical connections to the unit shall be at a single point terminal strip, housed in an electrical junction box for field wiring terminations.

#### d) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.6 Fan shall have dynamically balanced, centrifugal forward-curved, double wheel – double inlet fan wheel.  Fan wheel and scroll shall be constructed of galvanized steel, not plastic. .  Fan shaft shall have permanently lubricated ball bearings.

#### e) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.7 Motors shall be permanent split capacitor type with integral thermal overload protection. Motor shall be connected via a quick connect plug on the wiring harness.

#### f) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.8 Motor shall be capable of providing three speed operation by altering the selection of motor leads. Motor should be field adjustable for 120/277V or 208/240V service.

#### g) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.9 Cooling coil and heating coil shall be minimum 0.5” OD seamless copper tubes with mechanically bonded aluminum fins.  Minimum tube thickness to be 0.016”, and rated for a MAWP of 300 PSIG at 200 degrees F.

#### h) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.10 All coils shall be ARI 410 Certified and be tagged with an ARI 410 label.

#### i) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.11 Coil piping ends to be bare copper – no fittings installed in basic unit.

#### j) Meet or Exceed Requirement (circle one):                Yes	No

### 2.5.12 Coils equipped with manual air bleeders on the coil headers which are piped to the condensate drain pan to allow contained venting of unit.

#### k) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.13 Condensate pan shall be a minimum of 1” deep, constructed of a one piece, 22 gauge chromate coated galvanized steel, with a bonded internal epoxy resin coating. The pan shall be of an extended length to provide coverage across the length of the cooling coil and under the coil end fittings and control valves.

#### l) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.14 .Condensate pan shall be externally insulated with minimum 3/16” thick closed cell elastomeric foam insulation, meeting the same specification requirements as noted in item 2 above.

#### m) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.15 Filter rack and fan shall accommodate a minimum 1" thick pleated "throw-away" type filter, minimum filter performance rating of MERV 6.

#### n) Meet or Exceed Requirement (circle one): 	Yes	No

### 2.5.16 Internal connections and fittings shall be such that no condensation can drip free of containment at an entering Chilled Water temperature of 38 F.

# 2.5.17 FAN COIL UNIT CERTIFICATIONS:

## A. Methods of testing for Rating Fan Coil Air Conditioners: ASHRAE 79.

## B. Room Fan Coil Air Conditioners: ARI 440

## C. Safety Standards for Fan Coil Units and Room Fan Heater Units: ANSI/UL 883.

## D. Published sound power level data per ARI 350-86

## E. Noise Level Criteria shall comply with ARI 443.70

# 2.5.18 THERMAL DESIGN CRITERIA: Unless shown on the construction documents to be

# scheduled otherwise, the thermal design characteristics shall be as follows:

## A. Cooling: Coil shall be capable of meeting design requirements with an EWT of 45 F

## and a LWT of 58 F.

#### o) Meet or Exceed Requirement (circle one): 	Yes	No

## B. Heating: Coil shall be capable of meeting design requirements with an EWT of 150 F

## and a LWT of 130 F.

#### p) Meet or Exceed Requirement (circle one): 	Yes	No

3.0 Parts, Serviceability, and Value Added Questionnaire:

The following questions are considered important to University Operations and Maintenance personnel and thus are awarded points as noted up to a total value of 15 points for the questionnaire per the evaluative criteria contained in Section VI. Note that each question must be answered YES or NO to be considered responsive. No indication will be scored as a "NO" response. A space is provided for any brief explanatory comment. The comments will not be considered in scoring, but may support the selected response.

1. Are replacement parts readily available within 48 hours ARO?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

2. Is the primary filter access panel hinged?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

3. Is the service panel to access the motor and fan hinged?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

4. Is the service panel large enough to remove the service plate with the motor and blower as a single unit?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

5. Can the motor be easily separated from the fan wheels (using a set screw, clamp, or other compression fitting to hold the hub to the motor shaft) so the motor can be replaced separately (as opposed to a press fit, swedge or weld)?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

6. Can all major components – motor, fan wheels, filter, electrical wiring and harness – accessible from the primary service panel?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

7. Is the motor design and manufacture such that it is available only as an OEM part (it is not an industry standard HVAC type part available thru non-OE suppliers)?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

8. Are filters an industry standard cartridge size?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

9. Are the condensate drain pans made of a plastic or other non-corrodible material?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

10. Does the vendor support the factory installation of owner furnished control valves?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

11. Does the vendor support the factory installation of an owner furnished controller, including mounting of control power transformer, and wiring to the controller?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

12. Does the vendor support factory installation of other control accessories such as a supply water temperature sensor, return air temperature sensor, etc. including wiring to the controller?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

13. Is your company ISO 14001 certified for having corporate Environmental Management Systems in place?

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

14. Does your product contain post consumer recycled content? If YES, provide corporate documentation, and state the % content in the comments if known.

YES_________.      NO_________. 					 (1.0)

Comment:_______________________________________________

_______________________________________________

15. State where the final assembly of the product occurs, and is shipped from.

Comment:_______________________________________________ (1.0)

_______________________________________________

If necessary, feel free to enclose additional pages of text pertinent to the above questionnaire. Please note to which Section and question you are replying.

The University reserves the right to require a demonstration of products prior to award of the contract, For the purpose of validating answers to the questions in Section 3.0.

4.0 Innovation and Quality

The University of Arkansas wants to encourage innovation and recognize products that have best in class features. Up to 10 points can be awarded subjectively by the selection committee for products that differentiate themselves from the other products in the market. To be considered for the award of points based on Innovation and Quality, suppliers must provide the justification and information noted to be considered. Further this section will also be used to assess the overall compliance of the products in how they meet or exceed the minimum specification requirements.

Provide a narrative description of the features or functionality that distinguishes the product from the balance of the market. Include drawings, specifications, photographs, white papers, or other documentation that supports the innovative feature.

5.0 Pricing

Quote price of quantity one (1) each of all of the following

### All quoted equipment prices shall be FOB, The University of Arkansas, Central Supply Receiving Dock. Freight for equipment based on discounts from list shall be quoted separately at the time of order.

### Pricing shall be the same for either both-right hand, both-left hand, or one each-hand configuration for the stub out direction of cooling and heating coil piping

1. Horizontal Concealed:

200	 CFM 	$____________________

400	 CFM 	$____________________

600	 CFM 	$____________________

800	 CFM 	$____________________

1000	 CFM 	$____________________

1200	 CFM 	$____________________

2. Horizontal Exposed:

200	 CFM 	$____________________

400	 CFM 	$____________________

600	 CFM 	$____________________

800	 CFM 	$____________________

1000	 CFM 	$____________________

1200	 CFM 	$____________________

3. Vertical Exposed:

200	 CFM 	$____________________

400	 CFM 	$____________________

600	 CFM 	$____________________

800	 CFM 	$____________________

1000  CFM         $____________________

1200	 CFM 	$____________________

4. Slant Top:

200	 CFM 	$____________________

400	 CFM 	$____________________

600	 CFM 	$____________________

800	 CFM 	$____________________

1000	 CFM 	$____________________

1200	 CFM 	$____________________

5. Low Boy:

200	 CFM 	$____________________

400	 CFM 	$____________________

600	 CFM 	$____________________

800	 CFM 	$____________________

1000	 CFM 	$____________________

1200	 CFM 	$____________________

Total of all prices $ ________________________________________.

BID WILL BE AN ALL OR NONE BASIS.

- Please note Brand and Model no. (s) for each. Use additional pages as necessary

- Provide electronic submittal documents for each of the (5) five FCU types based on

the 600 CFM size.

6. 	Percent Multiplier against List Price for Other Base

FCU Sizes and Configurations: __________________%_ ( 8 points)

For all other sizes and / or configurations not listed above, provide the Multiplier to be applied against list price for the complete equipment package. The multiplier against the list price will determine the sell price to the University.

7. Provide a copy of your GSA pricing letter which shows your GSA multiplier, and identify what official document is used to identity list pricing for the purpose of GSA. Note this letter will be classified as confidential information and not subject to FOIA.

8. 	Percent Multiplier against List Price for

Accessories and Options: __________________%_( 4 points)

For accessories and options not listed as a part of the base equipment minimum specification requirements, provide the Multiplier to be applied against list price for these options when ordered with a complete equipment package. The multiplier against the total list pricing of the options will determine the sell price to the University, and be added to the base equipment IDIQ price.

9. 	Percent Multiplier against List Price for Parts: __________________%_( 2 points)

For replacement and repair parts, provide the Multiplier to be applied against list price for these replacement and repair parts. The multiplier against the list price will determine the sell price to the University added to the base equipment price.

10. 	Percent Multiplier against List Price for

Volume Purchase Discounts: ____________See %_below (6 points)

In the event that the University determines it is in its best interest to place larger orders for units, note any additional discount to be applied to the TOTAL VALUE OF THE ORDER (TVOO). The TVOO will be established by first determining the value of the standard FCU’s at the quoted IDIQ pricing (FOB UA), then including any non-standard sizes or configurations, options, accessories at their respective discounts from list pricing, and adding quoted freight charges. Based on the TVOO, the following Volume Purchase Discount Multiplier would then be applied to find the Sell Price.

TVOO 	Greater than or equal to $25,000, but less than $50,000			%

TVOO 	Greater than or equal to $50,000, but less than $100,000			%

TVOO 	Greater than or equal to $100,000						%

6.0 Evaluation Information

The University will utilize an evaluation team for the evaluation of this RFP. The evaluation will include the overall response to the RFP and that includes Pricing, Lead Time, Serviceability and Parts Availability Questionnaire, Manufacturing Specifications Questionnaire and Innovation.

This Proposal will be awarded as an All or None contract. Award will be made to the vendor who receives the most points based upon the following evaluation criteria.

Evaluation Criteria:

1. Defined Unit Pricing: Lowest grand total on cost will receive 50 points Section  5.0 Items 1, 2, 3, 4 and 5. Remaining bids shall receive points in accordance with the following formula:

(a ÷ b) (c) = d

Where:

a = the lowest cost bid

b = the second (third, fourth, etc.) cost bid

c = 70 (the maximum number of points allowed for cost)

d = number of points allocated to

2. Other Unit, Options, Material, and Volume Pricing: 20 points Section  5.0 Items 6, 7, 8, 9 and 10.

The lowest list price multiplier against list price shall receive the specified total number of points for each item. The remaining bids shall receive points in accordance with the formula listed above under Criteria 1.

3. Lead Time: 5 points - The University expects lead time to conform to the industry norm of six (6) weeks from the receipt of order to delivery at our receiving dock.

Your standard lead time in weeks ___________________________________.

4. Serviceability and Parts Availability Questionnaire 15 points Section 3.0.

5. Innovation: design and/or function. 10 points Section  4.0. Describe the relevant features and Patent no. (s) Or Patents Pending. Enclose a separate document or brochure.

Total Points       100 Points.

7.0 Warranty

All new equipment shall have a parts and labor warranty for a minimum period of one (1) year from date of receipt at the University of Arkansas, Central Supply Receiving Dock, or one (1) year from the date of contract substantial completion if furnished to a contractor for installation on a project.

Any questions regarding this RFP should go to Sam Emerson at 479-575-6172 or semerson@uark.edu.

Time of Perfor	Time of Performance

Time is of th             Time is of the essence in the rendering of services hereunder.  Proposer agrees to perform all obligations and rendering of services set forth in this RFP.

## Contracting Authority

Contractor shall perform all services as an independent Contractor and shall discharge all of its liabilities as such.  No acts performed or representation made, whether written or oral, by Contractor with respect to Third Parties shall be binding to the University.

Default

In the event t           In the even the Proposer fails to carry out or comply with any of the Terms and Conditions of the contract with the University, the University may notify the Proposer of such failure or default in writing and demand that the failure or default be remedied within ten (10) working days; and in the event the Proposer fails to remedy such failure or default within the ten (10) working day period, the University shall have the right to cancel the contract upon thirty (30) days written notice.

The cancellation of the contract, under any circumstances whatsoever, shall not effect or

relieve Proposer from any obligation or liability that may have been incurred or will be

incurred pursuant to the contract and such cancellation by the University shall not limit

any other right or remedy available to the University by law or in equity.

## Indemnification

Contractor agrees to indemnify and hold harmless the University and its officers and employees from any claim, damage, liability, injury, expense, or loss, including defense cost and attorney’s fees arising out of Contractor’s performance under this Agreement or as a consequence of the existence of this Agreement.

## Permits and Licenses

Contractor shall, at its sole expense, procure and keep in effect all necessary permits and licenses required for its performance under this Agreement, and shall post or display in a prominent place such permits and/or  notices as are required by law.

Termination

In the event that the Contractor shall fail to maintain or keep in force any of the terms and conditions of the Contract, the University may notify the vendor in writing of such failure and demand that the same be remedied within Ten (10) days.  Should the Contractor fail to remedy the same within said period, the University shall then have the right to terminate the Contract by giving the Contractor thirty (30) days written notice.

Right to Audit

At any time during the term of the agreement and for a period of four (4) years thereafter the University duly authorized audit representative, at its expense and at the reasonable times, reserves the right to incrementally audit Proposer’s records and manufacturer’s pricing relevant to all pricing provided under this agreement.  In the event such an audit by the University reveals any error/overpayments, the Proposer shall refund the University the full amount of such overpayments within thirty (30) days of such audit findings, or the University at its option, reserves the right to deduct such amounts plus interest owing the University from any payments due Seller.

Acceptance of Products and Services

All products furnished and all services performed under this agreement shall b

to the satisfaction of the University and in accordance with the specifications, terms, and conditions of the agreement.  The University reserves the right to inspect the products furnished or the services performed, and to determine the quality, acceptability, and fitness of such products or services.

Severability

If one or more provisions of the resultant agreement, or the application of any provision to any party or circumstance is held invalid, unenforceable, or illegal in any respect, the remainder of the agreement and the application of the provision to other parties or circumstances shall remain valid and in full force and effect.

Insurance Requirements

The contractor shall maintain liability insurance and shall file certificates of insurance with the owner prior to commencement of work.  Insurance policies shall be written by a company or companies authorized to do business in the State of Arkansas.  The limits of liability of such insurance shall be written for not less than the following limits:

- Workers Compensation
Workers Compensation as required by the State of Arkansas

B.	Comprehensive General Liability  (including Premises-Operations; Independent Contractors’ Protective; Products and Completed Operations; Broad Form Property Damage):

- 1.	Bodily Injury - $1,000,000.00 each occurrence, $1,000,000.00 aggregate.

2.	Property Damage - $1,000,000.00 each occurrence, $1,000,000.00 aggregate.

a.	Products and Completed Operations Insurance shall be maintained for a minimum period of (1) one year after final payment $1,000,000.00 aggregate.

b.	Property Damage Liability shall provide X, C, and U coverage

c.	Broad Form Property Damage coverage shall include Completed Operations

C.	Contractual Liability

- 1.	Bodily Injury - $1,000,000.00 each occurrence, $1,000,000.00 aggregate.

2.	Property Damage - $1,000,000.00 each occurrence, $1,000,000.00 aggregate.

- Personal Injury, with Employment Exclusion deleted, $1,000,000.00 aggregate

- Comprehensive Business Automobile Liability (including Owned, Non-Owned, and Hired Vehicles)
Bodily Injury and Property Damage – combined single limit of $500,000 per occurrence.

NOTE: Failure to file certificates, or acceptance by the University of certificates of insurance which do not indicate the specified coverage shall in no way relieve the Contractor of his responsibility for maintaining adequate insurance.

### CONTRACT INFORMATION

The University of Arkansas may not contract with another party:

For a period of time which continues past the end of a fiscal year unless the contract allow cancellation by the Agency Purchasing Official upon 30 days written notice whenever there are no funded appropriations for the contract.

To pay any penalties or charges for late payment or any penalties or charges which in fact are penalties for any reason.

To indemnify, defend, or hold harmless any party for any liability and damages.

Upon default, to pay all sums to become due under a contract.

To pay damages, legal expenses or other costs and expenses of any party.

To continue a contract once the equipment has been repossessed.

To conduct litigation in a place other than Washington County, Arkansas.

To agree to any provision of a contract which violates the laws or constitution of the State of Arkansas.

A party wishing to contract with the University of Arkansas should:

Remove any language from its contract which grants to it any remedies other than:

The right to possession

The right to accrued payments

The right to expenses of deinstallation

The right to expenses of repair to return the equipment to normal working order, normal wear and tear excluded.

The right to recover only amounts due at the time of repossession and any unamortized nonrecurring costs as allowed by Arkansas law.

Include in its contract that the laws of the State of Arkansas govern the contract.

Acknowledge in its contract that contracts become effective when awarded by the Agency Purchasing Official.

The University of Arkansas may contract with another party:

To accept the risk of loss of the equipment and pay for any destruction, lost or damage of the equipment while the University has such risk, when the extent of liability for such risk is based upon the purchase price of the equipment at the time of any loss and the contract has required the University to carry insurance for such risk.

To lease any equipment for a period of time which continues past the end of a fiscal year provided that, in the event funds are not appropriated for the equipment described in the agreement, the Agency Purchasing Official may, upon thirty days written notice to the vendor/lessor, cancel the agreement regarding that equipment for which no appropriations are made, or, in the event that there are no funded appropriations from which payment can be made for the equipment described in the agreement, the Agency Purchasing Official may upon thirty (30) days written notice to the vendor/lessor, cancel this agreement as to that equipment for which there are no funded appropriations from which payment can be made for the equipment.

Non-Waiver of Defaults

Any failure of the University at any time, to enforce or require the strict keeping and performance of any of the terms and conditions of this agreement shall not constitute a waiver of such terms, conditions, or rights, and shall not affect or impair same, or the right of the University at any time to avail itself of same.

Governing Law

This agreement shall be construed and governed by the laws of the State of Arkansas.

General Campus Background for University of Arkansas

Established in 1871 as a land grant institution, the University of Arkansas is the only comprehensive doctoral degree granting institution in Arkansas. It is classified as a Carnegie Foundation Doctoral/Research University. The University campus includes 360 buildings on 357 acres. The University offers more than 230 undergraduate and graduate degrees in more than 150 fields of study in agricultural, food and life sciences, arts and sciences, business, education, engineering, architecture and law. As of Fall 2008, student enrollment was 18,648 (undergraduate 14,861, professional 398, graduate 3192, and non-degree 743; full-time 14,814 and part-time 4,380). The faculty count was 898, and staff count was 2864. The University is the flagship campus for the University of Arkansas System.

Proprietary Information

Proprietary Information submitted in response to this bid will be processed in accordance with applicable University of Arkansas Procurement procedures. All material submitted in response to this bid becomes the public property of the State of Arkansas and will be a matter of public record and open to public inspection subsequent to bid opening as defined by the Arkansas Freedom of Information Act. The respondent is hereby cautioned that any part of its bid that is considered confidential, proprietary, or a trade secret, must be labeled as such and submitted in a separate envelope along with the bid, and can only be protected to the extent permitted by Arkansas Law. Co-mingling of propriety/confidential and other bid information is NOT acceptable. Neither a bid, in its entirety, nor bid pricing will be considered propriety/confidential information after a proposal opening has been accomplished and awarded. Any information that will be included in any resulting contract cannot be considered proprietary/confidential.

Ethical Standards

“It shall be a breach of ethical standards for a person to be retained, or to retain a person, to solicit or secure a state contract upon an agreement or understanding for a commission, percentage, brokerage, or contingent fee, except for retention of bona fide employees or bona fide established commercial selling agencies maintained by the contractor for the purpose of securing business”

Technology Access

The Vendor expressly acknowledges that state funds may not be expended in connection with the purchase of information technology unless that system meets certain statutory requirements, in accordance with State of Arkansas technology policy standards relating to accessibility by persons with visual impairments.

Accordingly, the Vendor represents and warrants to University of Arkansas, Fayetteville that the technology provided to University of Arkansas for purchase is capable, either by virtue of features included within the technology or because it is readily adaptable by use with other technology, of: (1) providing equivalent access for effective use by both visual and nonvisual means; (2) presenting information, including prompts used for interactive communications, in formats intended for nonvisual use; and (3) being integrated into networks for obtaining, retrieving, and disseminating information used by individuals who are not blind or visually impaired.

For purpose of this paragraph, the phrase “equivalent access” means a substantially similar ability to communicate with or make use of the technology, either directly by features incorporated within the technology or by other reasonable means such as assisting devices or services which would constitute reasonable accommodations under the American with Disabilities Act or similar state or federal laws.  Examples of methods by which equivalent access may be provided include, but are not limited to, keyboard alternatives to mouse commands and other means of navigating graphical displays, and customizable display appearance.

If requested, the Vendor must provide a detailed plan for making this purchase accessible and/or a validation of concept demonstration.

Equal Opportunity Policy Disclaimer

ATTENTION BIDDERS

Act 2157 of 2005 of the Arkansas Regular Legislative Session requires that any business or person bidding, who is responding to a formal bid request, Request for Qualifications or qualifications, or negotiating a contract with the state for professional or consultant services, submit their most current equal opportunity policy (EO Policy).

Although bidders are encouraged to have a viable equal opportunity policy, a written response stating the bidder does not have such an EO Policy will be considered that bidder’s response and will be acceptable in complying with the requirement of Act 2157.

Submitting the EO Policy is a one-time requirement.  The University of Arkansas, Fayetteville Procurement Department, will maintain a database of policies or written responses received from all bidders.

Note: This is a mandatory requirement when submitting an offer as described above.

Please complete and return this form with your bid response.

Should you have any questions regarding this requirement, please contact this office by calling (479) 575-2551.

Sincerely,

Linda Fast

Linda Fast, APO, CPPO, CPPB

Manager of Procurement Services

University of Arkansas

To be completed by business or person submitting response: (check appropriate box)

____   EO Policy Attached

____   EO Policy previously submitted to University of Arkansas, Fayetteville

Purchasing Department

____   EO Policy is not available from business or person

Company Name

Or Individual: __________________________________________________________

Title:  _____________________________________Date:  ______________________

Signature:  ____________________________________________________________

University of Arkansas

Fayetteville, Arkansas

Procurement Department

321 Administration

Fayetteville, AR  72701

Tel:  479-575-2551

Fax:  479-575-4158

Act 157 of 2007 of the Arkansas Regular Legislative Session requires that any business or person responding to a Request for Proposal (RFP) for professional services, technical and general services or any category of construction in which the total dollar value is $25,000 or greater certify, prior to the award of the contract, that they do not employ or contract with any illegal immigrants.  Bidders are to certify online at:

http://www.dfa.arkansas.gov/offices/procurement/Pages/forms.aspx

This is a mandatory requirement.  Failure to certify may result in rejection of your proposal, and no award will be made to a vendor who has not so certified.  If you have any questions, please contact the Procurement Department.  Thank you.

Linda Fast

Linda Fast, APO, CPPO, CPPB

Manager of Procurement Services

************************************************************************************************************

TO BE COMPLETED BY BUSINESS OR PERSON SUBMITTING RESPONSE:

Please check the appropriate statement below:

_______	We have certified on-line that we do not employ or contract with any

illegal immigrants

Date on-line certification completed:  ___________________________________

_______	We have NOT certified on-line at this time, and we understand that

no contract can awarded to our firm until we have done so.

Reason for non-certification:  _________________________________________

| Name of Company |  |
| --- | --- |
| Mailing Address |  |
| City, State & Zip |  |
| Signature |  |
| Name & Title (printed or typed) |  |
| Date |  |