The Louisiana Technical College- Oakdale Campus will be accepting Sealed bids for an Instrumentation and Controls Trainer that will be a Hampden MODEL H-ICS-8189-4 or equivalent.

The trainer must provide experience in setting up, tuning, operating, and trouble-shooting actual instrument and control systems of the type used in the Power and Process industries. The unit must simulate different process loops, and provide instruction in the measuring and transducing of such physical variables as pressure, temperature, flow, and level.

Students and trainees learn instrumentation and control techniques of standard commercial manufacturers, such as Foxboro, and Rosemount. Various types of closed-loop control: on/off, proportional, proportional plus integral, and proportional plus integral plus derivative, as well as a variety of final control devices, including electrical, pneumatic and electronic are covered.

The system will consist of two clear process tanks (one for flow/temperature and one for level/pressure), two reservoir tanks, two pumps, and other instrumentation mounted on or inside a mobile bench. The trainer will provide measurement and control of flow, temperature, level and pressure utilizing microprocessor based control.

All shipping and handling costs will be the responsibility of the bidder.  Bid opening on February 5th @ 10am.

For further information please contact Randall Esters @ LTC Oakdale – (318) 335-3944 Ext 126

The trainer will consist of the following:

- Level Loop—In the level loop, water will be pumped through the delay loop to the level tank. The water level in the level tank will be controlled by changes in the control valve. The 4–20 mA input loop will consist of a level transmitter, recorder, and controller. The output signal will be a 4–20 mA control signal, driving the valve toward either the open or closed position.

- Pressure Loop—In the pressure loop, water will be pumped into a tank, creating an air pressure whose value depends on water level in process tank. The 4–20 mA input loop includes the pressure transmitter, recorder and controller. The 4–20 mA output loop will contain the controller recorder and controller recorder and I/P valve positioner.

- Flow Loop—In the flow loop, water will be pumped at a rate determined by the position of the control valve and of a hand-operated stop valve. Flow will be sensed by an orifice differential pressure transmitter. The 4–20 mA output loop contains the controller, recorder, and a current-to-pneumatic converter positioner to control the position of the valve.

- Temperature Loop—In the temperature loop, heated water temperature will be sensed by a temperature transmitter. Water temperature will be controlled by: (1) the voltage applied to the heater coil through the power controller; and (2) whether the water will be made to flow through the heat exchanger. A temperature transmitter  will drive the controller input. The 4–20 mA output loop will include the controller, recorder, and power controller. An additional contact-closure output will operate the three-way valve, or the valve may be manually switched to provide the process disturbance.

| SPECIFICATIONS |  |  |
| --- | --- | --- |
| Construction: |  | Mobile bench with doors and control panel. The bench will be finished in steel |
|  |  | and the control panel in instrument white enamel |
| Casters: |  | Two stationary, two swivel with locks |
| Bench Top: |  | 75" x 30" x 13/16". Unit consists of a 1/16" thick white plastic laminate |
|  |  | fastened to 3/4" thick marine plywood. |
| Instrumentation: |  | Foxboro microprocessor, single-station controllers with RS-485 |
|  |  | communications port |
|  |  | Foxboro 3-channel single-station electronic recorder |
|  |  | Smart d/p cell transmitters, level/flow |
|  |  | Smart electronic gauge pressure transmitter |
|  |  | Foxboro temperature transmitter |
| Plumbing: |  | All piping on the mobile bench will be clear PVC. Fittings are PVC and |
|  |  | piping inside the trainer will be copper. |
| Components: |  | Main circuit breaker with ground fault interrupter protection |
|  |  | Globe style control valve with I/P valve positioner |
|  |  | Pumps control switches |
|  |  | Oil-less air compressor switch |
|  |  | Heat exchanger manual/auto and on/off switches |
|  |  | Manual/Auto temperature control. |
|  |  | Oil-less air compressor rated 1.9 CFM at 100 psi complete with three gallon |
|  |  | tank and regulator with gauges |
|  |  | Storage tanks, each 11 gallon with fill and drain ball valve with hose fitting. |
|  |  | Included with the heated storage tank will be a temperature switch (set for 120°F |
|  |  | for maximum hot water temperature) and a low level float switch. |
|  |  | Clear process tanks, each 5 gallon with fittings for overflow, manual load |
|  |  | needle valves, level, pressure, flow, temperature transmitters, and overflow |
|  |  | switches. Pressure tank includes a pressure switch and a pressure relief |
|  |  | valve. |
|  |  | Pumps, rated 360 gph at 9' head |
|  |  | Three-way valve with 50' dead time flow circuit |
|  |  | Orifice plate assembly with quick-connect fittings |
|  |  | Power cord, 8ft. |
|  |  | Cord storage rack |

FAULTS

Fault package will provide 12 instructor insertable faults with controls located in a locked compartment. The insertable faults will be in: Level Transmitter Pressure Switch Heater, Pumps 1 & 2, Heat Exchanger, Baumann Control, Valve, Heat Exchanger Fan, Air Compressor, High Level Switch, 3-Way Asco Valve and Controllers.