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	Coastal Carolina University
Office of Procurement & Business Services
642 Century Circle
P.O. Box 261954
Conway, SC 29526
Telephone: (843) 349-2189
	
Request for Quotation
Services


THIS IS NOT AN ORDER

	Quotation must be received
[bookmark: Text1]No Later Than: 11:00am (Time)
[bookmark: Text2][bookmark: Text3][bookmark: Text4]    10⁄ 13⁄ 2011 (Date)
	Send quotation to above address
Attention of:
[bookmark: Text5]Vicki Williams
	Quotation Number:

[bookmark: Text6]1225VW
	Issue Date:

09⁄ 29⁄ 2011



	[bookmark: Text7]Name:     
[bookmark: Text71]Address:      
[bookmark: Text72]                      

[bookmark: Text73]Attention:      
FAX: (     )      -     
TELEPHONE: (     )      -     


Purchase Order Address:	Please quote your lowest delivered price for the service(s) below. The Office of Procurement & Business Services reserves the right to reject any or all quotes and to waive any or all technicalities.
1.  If service cannot be furnished, indicate by NO QUOTE.
2.  All quotes must be signed by the Offeror’s representative to be valid.
3.  South Carolina sales tax will not be paid on labor.
[bookmark: Text8][bookmark: Text9]4.  FAXED QUOTES ARE ACCEPTABLE; FAX TO: (843) 349 2912.
[bookmark: Text10]5.  EMAIL QUOTES ARE ACCEPTABLE; EMAIL TO: vicki@coastal.edu.
6. The attached Terms & Conditions apply to all quotes and supersedes Offeror’s 
     Terms & Conditions.

[bookmark: Text11][bookmark: Text12][bookmark: Text17]Federal I. D. or SSN:      		SC Minority Certification Number (if applicable):         		Email:      		
[bookmark: Text13][bookmark: Text59][bookmark: Text14][bookmark: Text15][bookmark: Text16]Submitted By:       (Name)	*Signature:      _________________________________   	Telephone: (     )      -     
*Important: If you choose to return your response via email, no additional signature is required. It will be presumed that the sender has the ability to legally bind their organization or company to a contract. The name typed in the “Signature” line will be considered equivalent to an ink signature.
	Description of Services: Coastal Carolina University is seeking to establish a contract to provide Preventative Maintenance, Inspection and Emergency Repair Service of Generator’s in accordance with the terms and conditions as per specifications listed herein.

Purpose:  The purpose of this contract is to provide Coastal Carolina University expert maintenance and repair services to all the generator equipment listed in Bidding Schedule.  The equipment shall be kept in fine-tuned condition by appropriate repairs, maintenance and adjustments for peak effectiveness and efficiency; and responsiveness on the part of the contractor when any repair or adjustment is necessary.

Equipment Inspection:  Prior to bidding, it shall be the responsibility of the bidder to visit the job site and inspect each piece of equipment to establish to his satisfaction the condition of the equipment to be maintained.  This equipment is offered in “as is” condition. Should any equipment require repairs to place it in acceptable condition, Contractor shall submit, with his bid, a written report on each piece of equipment not meeting this requirement, along with the cost or the necessary repairs.  If a report is not submitted, the University shall assume that repairs are unnecessary and all equipment is in satisfactory condition for Contractor to maintain.  Correction of deficiencies claimed to exist prior to award of contact will not be authorized. If in the opinion of University personnel such repairs are necessary, the Contractor may be requested to perform all or part of the repairs.  However, Coastal Carolina University reserves the right to have identified repairs performed by another party prior to start of the contract.

Responsibilities of Servicing Contractor:  The Servicing Contractor shall perform the maintenance as herein specified by trained, skilled, professional craftsmen who wear clean and neat company uniforms and who are familiar with inspection, maintenance and repair procedures as identified in the specifications listed herein.  

Contractor shall be responsible for the acts of its employees and agents and agrees to take all necessary measures to prevent injury and loss to persons present on University premises. 

Contractor shall be responsible for all damages to persons or property caused by Contractor or any of its agents or employees. 

Contractor shall promptly repair any damage that it, its employees or agents may cause to the University’s premises or equipment; on Contractor’s failure to do so, the University may repair such damage and Contractor shall reimburse the University promptly for the cost of the repair.

Contractor shall comply with all applicable University policies, i.e. Parking, Landscaping, etc.  

Contractor shall adhere to standards as regulated by OSHA, EPA, DHEC, and other regulatory agencies.

Qualifications:  The competency and experience of the servicing contractor is a major concern for the Coastal Carolina University, therefore proposals will only be considered from companies who can affirmatively demonstrate and give evidence showing that they are an established mechanical servicing contractor providing electrical/mechanical maintenance service on Generating systems of comparable size and complexity. 

Offeror shall submit (3) reference accounts where the services offered were similar to the services requested in this solicitation. Information should include name address, telephone number and title of person to contact for inquiry as to Offeror’s experience and performance. Include past performance for similar activities for the STATE on previous projects, if applicable. Reference account must not be affiliated with Offeror. The University reserves the right to contact any, all or none of the reference provided pursuant to this section.

Scope of Services:  The servicing contractor shall furnish all labor, materials, supplies, service vehicles, communication needs, parts, tools, test equipment, special equipment lubricants, and labor supervision necessary to provide preventive maintenance and emergency repair services as described herein. These services shall include, generator equipment inspections, examinations, lubrication, testing, cleaning and adjusting. The servicing contractor shall notify Coastal Carolina University’s representative of improper operating parts, which will be required in written form with details, and assist with determining the correct repair and/or replacement action, with an accompanying quote for materials (parts) and labor.  The University reserves the right to request a second opinion from another source.

Quarterly Inspection and Maintenance:  The servicing contractor shall provide labor, material, and shut down schedule to perform quarterly operational inspections on each generator listed in the Bidding Schedule. The service shall consist of the following:

1.  Inspect cooling system hoses;
2.  Check engine heater operation; 
3.  Check/adjust belts;
4.  Check engine and generator gauge and meter operation; 
5.  Check generator set for fuel, oil and coolant leaks;
6.  Check air intakes and outlets and emergency stop;
7.  Check transfer/day tank operation;
8.  Inspect silencer;
9.  Check output voltage and adjust as necessary; 
10.   Check battery charger operation and charger rate;
11.   Check battery connections and specific gravity;
12.   Lubricate louver linkage as necessary;
13.   Visually inspect transfer switch and accessory operation;
14.   Check anti-freeze mixture, add fluid and adjust mixture as     necessary;
15.   Check cooling system hoses;
16.   Provide written report after each inspection including any    recommendations for predictive maintenance or    improving performance.

Annual Preventative Maintenance Service:  In addition to the quarterly monthly preventive maintenance items listed above, the Contractor shall perform the following services one (1) time per year for all generators referenced in the Bidding Schedule:

1. Replace and add oil filters;
2.    Change fuel filters;
        3.    Check coolant level;
        4.    Test anti-freeze and adjust as necessary;
5.    Check transfer switch and accessory operation;
6.   Check unit controller functions and shutdown;
7.   Emergency system operation w/load transfer;
8.   Test and condition diesel fuel to eliminate water and sludging;
9.   Replace air filter;
10.   Tune engine, if required

Corrective Maintenance and Scheduled Repairs: Servicing Contractor shall furnish a written quotation (faxes and PDF acceptable) prior to the commencement of the work. This quote shall separate labor and materials charges. The agency will not be obligated to issue Other Repair work to the Contractor and may seek quotations from other contractors. The agency will exercise care with regards to work performed by other contractor(s) and that impact on warranties and guaranties.
A. The Servicing Contractor agrees to correct, by repair or replacement at no additional cost, any defects in material or workmanship installed under this contract which may develop under normal use within one (1) year from installation.
Unscheduled Service Calls:  The Servicing Contractor shall be responsible for all unscheduled service calls and must be prepared to begin work to make repairs within two hours of request by University personnel. The technician shall be required to check in and out at the Facilities Maintenance Office for all unscheduled calls and are required to have their service ticket signed by a Facilities Maintenance staff member.  A copy of the service ticket with the complete description of work performed must be left at the Facilities Maintenance Office after each visit.  Contractor shall provide 24 hour standby service, seven (7) days per week, and shall provide backup portable generator power as necessary. 

Hours and Manners of work:  All preventative maintenance, repairs, routine adjusting and service procedures will be performed during regular working hours, five (5) days per week, Monday through Friday. Regular hours are from 8:00 A.M. to 5:00 P.M.

Addition / Deletion:  Generators to be serviced and maintained under this contract are specified on the Bid Schedule. Any unit added or deleted by the University from said list will result in an equitable adjustment to the contract price. If added, the price will be negotiated by the parties. If a unit is deleted, the price as then in effect on said individual unit will be prorated over the remainder of the contract period and so subtracted from the contractual amount due under this contract.
Reports: The Contractor is required to submit a written, detailed, quarterly report describing the cost per generator, the work performed and recommendations for corrective maintenance not covered by the preventative maintenance service. The University will review reports and approve any corrective maintenance or repairs that may be required or suggested. Additional work not covered by this Service Agreement will not be performed until expressly authorized by the University.
Payment: Payment will be made on a quarterly basis as charges are incurred.

Contract Period:  November 1, 2011 through October 31, 2012

Site Visit:  Appointment for a site visit may be made by contacting Ron Gardner at 843-349-2465.

Award Criteria: 
· Award will be made to the lowest responsible and responsive bidder.
· Award will be made to one Offeror.
· In determining award, unit prices will govern over extended prices unless otherwise stated. 

License: The Contractor must be licensed in South Carolina as a Mechanical Contractor  in the following classifications to perform work under this agreement:
· Certified Generator Technicians Certification Required. Technicians must be able to perform basic to medium level troubleshooting on commercial power supply side, transfer switches, control software and related control hardware. Contractor must also be able to supply high level electrical technicians if the need should arise.    

Service Facility:  The successful Contractor must have a service facility within a thirty (30) mile radius of Coastal Carolina University.




BID SCHEDULE – SERVICE CONTRACT   RFQ # 1225VW
	[bookmark: Text61]By submitting a bid to Coastal Carolina University, the Contractor agrees to abide by the specifications as written and understand that modifications will not be acceptable unless prior approval is received from Vicki Williams in the Office of Procurement and Business Services.

		Building

	Mfg.
	Description: Provide Generator Maintenance and Repair Service in accordance with terms, conditions, and specifications as described in RFQ #1125VW.  None of the following generators are currently under warranty.
	Cost Per Quarter
	Cost Per 
Year 

	Humanities
	Kohler
	Model # 100 RZ     S/N 0693420     Spec. # PA-18744
kW:  100     Phase:  3     Volts:  277/480     Fuel: NG Eng. Mfg.:  Ford     Model # LGS-8751-6005-A  Engine S/N 3900 HZA-3900-QBA
Transfer Switch #1, Model # GLN-166341-150     S/N K0693323, Volts:  277/480     Amps:  150     Poles:  3   Wires:  4
Transfer Switch #2, Model # GLN-166341-0080     S/N K0690883, Volts:  277/480     Amps:  150     Poles:  3   Wires:  4
	$     
	$     

	Wall
	Kohler
	Model # 50 RZGB    S/N 0752831     Spec. # GM 21302-GAI
 kW:  50     Phase:  3     Volts:  277/480     Fuel: NG
Engine Mfg.:  Kohler     Model # 5.0L  S/N  5.0L-005243   
Transfer Switch #1, Cummins (Onan) Model # OTCU 150G     S/N I910421103, Volts:  277/480     Amps:  150     Poles:  3     Wires:  4  Hertz: 60
	$     
	$     

	Residence Halls
	Generac
	Model # 95A03434-S    S/N 2022052     kW:  75     Phase:  3     Volts:  120/208     Fuel: NG Eng. Mfg.:  350 Chevy     Model:  5 Liter
 Transfer Switch #1, Model # 95A03434-W     S/N 30152, Volts:  120/208     Amps:  150     Poles:  3     Wires:  4
	$     
	$     

	Wall
(ITS)
	Onan
	Model # GGLB-5769375    S/N G060943050     kW:  150  Amps: 225.2    Phase:  3  Wire: 4   Volts:  120/208     Fuel: Diesel  Hertz: 60
Transfer Switch #1, Model #  OPTCA-5769373/A   S/N  GO60943733
 Volts: 480    Amps:  125  Phase: 3      Poles:  3   Wires:  4    Hertz:  60
Transfer Switch #2, Model #  OPTCb-5769374/A   S/N  GO60943732
 Volts: 480    Amps:  260  Phase: 3      Poles:  3   Wires:  4    Hertz:  60

	$     
	$     

	
Lift Station
	Cummins
	Model # DGCB-569738/T     S/N L040723270     kW:  60       Amps: 90.2    Phase:  3     Wire:  4  Volts:  277/480     Fuel: Diesel   Hertz:  60
Eng. Mfg.:  Cummins     Model # 4BTA3.9-G5    Engine S/N 46451113
Transfer Switch #1, Model # OTECA-57112119/A    S/N D050772256
Volts:  277/480     Amps:  125    Phase:  3     Poles:  3  Wires:  4    Hertz:  60 
 
	$     
	$     

	Singleton
	Cummins
	Model # DGBB-5734954/K     S/N G050803675    kW:  35   Amps: 121.4    Phase:  3    Wire:  4   Volts:  120/208    Fuel: Diesel   Hertz: 60
Eng. Mfg.:  Cummins     Model # 4B3.9    Engine S/N 46450422
Transfer Switch #1
Model # OTECB-5734446/A    S/N F050793810
Volts:  120/208     Amps:  150    Phase:  3     Poles:  3  Wires:  4    Hertz:  60
  
	$     
	$     

	Atheneum Hall
	Cummins
	Model # DGDA-5734984     S/N G050800789     kW:  80       Amps: 277.6       Phase:  3     Wire:  4     Volts:  120/208     Hertz:  60   Fuel: Diesel  Eng. Mfg.:  Cummins     Model # 6BTA5.9-G4    Engine S/N 46491276
Transfer Switch #1  Model # OTECB-5734437    S/N F050793811
Volts:  120/208     Amps:  400    Phase:  3     Poles:  3  Wires:  4    Hertz:  60 
 
	$     
	$     

	Brooks Stadium
	Cummins
(Onan)
	Model # GGHH-7227369     S/N H080201431     kW:  100       Amps: 150.4       Phase:  3     Wire:  4     Volts:  277/480        Fuel: NG
Eng. Mfg.:  Ford      Model # WSG-1068    Engine S/N E182A 070508 1286152
Transfer Switch #1  Model # OTPCB-7226934/A    S/N G080197669  Volts:  480     Amps:  150   Phase:  3     Poles:  3     Wires:  4    
	$     
	$     

	
	
	TOTAL ANNUAL COST

	
	$     


For information only, Offerors must furnish the hourly wage rates (including mileage) for the provision of all necessary labor, materials, equipment, and supplies for unscheduled service calls/repairs which shall be defined as work not included as preventative maintenance:  
Provide all necessary labor, materials, equipment, and supplies for unscheduled service calls/repairs as needed to be billed at the following rates (mileage to be included in hourly rates):
	
	Hourly Wage for Mechanic
	Hourly Wage for
 Helper

	Regular Hours
	$     
	$     

	Overtime hours
	$     
	$     

	Sunday & Holidays
	$     
	$     

	Contractor’s Markup (not to exceed 25% of Contractor’s cost)
	                       %

	Contractor’s Markup on Industry Published Rental Rates for Generators
	                       %







GENERAL CONDITIONS
DEFAULT: In case or default by the Contractor, Coastal Carolina University reserves the right to purchase any or all items in default in the open market, charging the Contractor with any additional costs. The defaulting Contractor shall not be considered a responsible Contractor until the assessed charge has been satisfied.

All amendments to and interpretation of this RFQ shall be in writing. The procurement officer shall not be legally bound by any amendment or interpretation that is not in writing.

Any contract entered into by Coastal Carolina University resulting from this quotation shall be subject to cancellation at the end of any fiscal or appropriated year unless otherwise provided by law.

Payment will be made in accordance with Section 11-35-45 of the South Carolina Consolidated Procurement Code and Disbursement Regulations. Delay in receiving invoices, as well as errors and omissions on the invoices, will be considered just cause for withholding payment without losing discount privileges. The University reserves the right to withhold payment or make such deductions as may be necessary to protect the University from loss or damage because of defective work, claims, damages or to pay for repair of correction of materials furnished hereunder.

Quoted prices must remain firm for a period of thirty (30) days beyond the Request for Quotation deadline. 

Unit prices will govern over extended prices unless otherwise stated.

Coastal Carolina University shall consider payment discounts in the award of this contract when such discounts are for thirty (30) days or more after final inspection and acceptance of contract requirements. Payment discounts for less than thirty days are encouraged but shall not be a factor in award determination. Please state your discount terms using the above referenced information as the University’s position on the matter.

All materials and products offered must be guaranteed to meet and comply with the requirements all the specifications, terms and conditions indicated or referred to.

The award will be made in accordance with Section 11-35-1550 (b)of the South Carolina Consolidated Procurement Code.

The University reserves the right to reject any and all quotations and to cancel the solicitation; waive any and all technicalities; the University reserves the right to reject any quotation in which the delivery tine indicated to be of substantial length to cause disruption and/or delay in operation for which the item(s) is/are intended; ambiguous quotations which are uncertain as to terms, delivery, quantity or compliance with specifications may be rejected.

The contractor assumes sole responsibility and shall hold harmless Coastal Carolina University, its directors, officers, employees and agents from and against any and all claims, actions or liabilities of any nature which may be asserted against them by third parties in connection with the performance of the successful Contractor, its directors, officers, employees and agents under this agreement. Coastal Carolina University agrees to accept responsibility for claims, actions or liabilities resulting from negligent acts of its employees occurring within the scope of their employment which may be asserted against them by third parties in connection with the performance of Coastal Carolina University, its members, directors, officers, employees and agents under this agreement.

Contractor agrees not to refer to award of this contract in commercial advertising in such a manner to state or imply that the products or service provided are endorsed or preferred by the user.

Upon award of a contract under this quotation, the person, partnership, association or corporation to whom the award is made must comply with the laws of South Carolina that require such person or entity to be authorized and/or licensed to do business in this State. Notwithstanding the fact that applicable statutes may be exempt or exclude the successful Contractor from requirements that it be authorized and/or licensed to do business in this State, by submission of this signed quote, the Contractor agrees to subject itself to the jurisdiction and process of the courts of the State of South Carolina as to all matters and disputes arising or to arise under the contract and the performance thereof, including any questions as to the liability for taxes, licenses or fees levied by the State.

Termination: Subject to the provisions below, the contract may be terminated for any reason by the University providing a thirty-day advance notice in writing is given to the contractor.

Termination for Convenience: In the event that this contract is terminated or cancelled upon request and for the convenience of the University may negotiate reasonable termination costs, if applicable.

Termination for Cause: Termination by the University for cause, default, or negligence on the part of the Contractor shall be excluded from the foregoing provisions; termination costs, if any, shall not apply. The thirty day advance notice requirement is waived and the default provision in this bid shall apply.

HIPAA Law: The Contractor agrees that to the extent that some or all of the activities within the scope of this Contract are subject to the Health Insurance Portability Accountability Act of 1996, P.L. 104-91, as amended (“HIPAA”), or its implementing regulations, it will comply with the HIPAA requirements and will execute such agreements and practices as the Coastal Carolina University may require to ensure compliance. Additional information may be viewed at: http://www.sc.edu/hipaa/
   	
SPECIAL CONDITIONS
CONTRACTOR'S LIABILITY INSURANCE (JANUARY 2006): (1) Contractor shall purchase from and maintain in a company or companies lawfully authorized to do business in South Carolina such insurance as will protect the contractor from the types of claims set forth below which may arise out of or result from the contractor's operations under the contract and for which the contractor may be legally liable, whether such operations be by the contractor or by a subcontractor or by anyone directly or indirectly employed by any of them, or by anyone for whose acts any of them may be liable: (a) claims under workers' compensation, disability benefit and other similar employee benefit acts which are applicable to the work to be performed; (b) claims for damages because of bodily injury, occupational sickness or disease, or death of the contractor's employees; (c) claims for damages because of bodily injury, sickness or disease, or death of any person other than the contractor's employees; (d) claims for damages insured by usual personal injury liability coverage; (e) claims for damages, other than to the work itself, because of injury to or destruction of tangible property, including loss of use resulting there from; (f) claims for damages because of bodily injury, death of a person or property damage arising out of ownership, maintenance or use of a motor vehicle; (g) claims for bodily injury or property damage arising out of completed operations; and (h) claims involving contractual liability insurance applicable to the Contractor's obligations under the provision entitled Indemnification – Third Party Claims.
(2) Coverage shall be written on an occurrence basis and shall be maintained without interruption from date of commencement of the work until date of final payment.  Coverage must include the following on a commercial basis: (i) Premises – Operations, (ii) Independent Contractor’s Protective, (iii) Products and Completed Operations, (iv) Personal and Advertising Injury, (v) Contractual, including specific provision for contractor’s obligations under the provision entitled Indemnification – Third Party Claims, (vi) Broad Form Property Damage including Completed Operations, and (vii) Owned, Non-owned and Hired Motor Vehicles.
(3) The insurance required by this paragraph shall be written for not less than the following limits of liability or as required by law, whichever coverage is greater:
COMMERCIAL GENERAL LIABILITY:
General Aggregate (per project) $1,000,000
Products/Completed Operations $1,000,000
Personal and Advertising Injury $1,000,000
Each Occurrence $1,000,000
Fire Damage (Any one fire) $ 50,000
Medical Expense (Any one person) $ 5,000
BUSINESS AUTO LIABILITY (including All Owned, Non-owned, and Hired Vehicles):
Combined Single Limit $1,000,000
                        OR
Bodily Injury & Property Damage (each) $750,000
WORKER’S COMPENSATION:
State Statutory
Employers Liability $100,000 per Acc.
$500,000 Disease, Policy Limit; $100,000 Disease, Each Employee
(4) Required Documentation. (a) Prior to commencement of the work, contractor shall provide to the state a signed, original certificate of liability insurance (ACORD 25). The certificate shall identify the types of insurance, state the limits of liability for each type of coverage, include a provision for 30 days notice prior to cancellation, name every applicable using governmental unit (as identified on the cover page) as a Certificate Holder, provide that the general aggregate limit applies per project, and provide that coverage is written on an occurrence basis. (b) Prior to commencement of the work, contractor shall provide to the state a written endorsement to the contractor’s general liability insurance policy that (i) names every applicable using governmental unit (as identified on the Cover Page) as an additional insured, (ii) provides that no material alteration, cancellation, non-renewal, or expiration of the coverage contained in such policy shall have effect unless the named governmental unit(s) has been given at least thirty (30) days prior written notice, and (iii) provides that the Contractor’s liability insurance policy shall be primary, with any liability insurance of the state as secondary and noncontributory. (c) Both the certificate and the endorsement must be received directly from either the contractor's insurance agent or the insurance company.
(5) Contractor shall provide a minimum of thirty (30) days written notice to every applicable using governmental unit of any proposed reduction of coverage limits (on account of revised limits or claims paid under the General Aggregate) or any substitution of insurance carriers.
Additional Insured: Coastal Carolina University (CCU) shall be shown as an Additional Insured in the Description of Operations section. The contractor/vendor is required to add CCU to its Commercial General Liability and Employers Liability insurance policies with the following language: 	“Coastal Carolina University, including its current and former trustees, officers, directors, employees, volunteer workers, agents, assigns and students, is added to this policy as additional insured.”
[bookmark: End_07BTeS_00081][bookmark: Start_07BTeS_00082][bookmark: _Toc241389936](6) The state's failure to demand either a certificate of insurance or written endorsement required by this paragraph is not a waiver of contractor's obligations to obtain the required insurance. 
CONTRACTOR PERSONNEL (JANUARY 2006): The Contractor shall enforce strict discipline and good order among the Contractor's employees and other persons carrying out the Contract. The Contractor shall not permit employment of unfit persons or persons not skilled in tasks assigned to them.
[bookmark: End_07BTeS_00082][bookmark: Start_07BTeS_00083][bookmark: _Toc241389937]CONTRACTOR'S OBLIGATION – GENERAL (JANUARY 2006): The contractor shall provide and pay for all materials, tools, equipment, labor and professional and non-professional services, and shall perform all other acts and supply all other things necessary, to fully and properly perform and complete the work. The contractor must act as the prime contractor and assume full responsibility for any subcontractor’s performance.  The contractor will be considered the sole point of contact with regard to all situations, including payment of all charges and the meeting of all other requirements.
[bookmark: _Toc241389938]CONTRACTOR’S USE OF STATE PROPERTY (JAN 2006): Upon termination of the contract for any reason, the State shall have the right, upon demand, to obtain access to, and possession of, all State properties, including, but not limited to, current copies of all State application programs and necessary documentation, all data, files, intermediate materials and supplies held by the contractor. Contractor shall not use, reproduce, distribute, display, or sell any data, material, or documentation owned exclusively by the State without the State's written consent, except to the extent necessary to carry out the work.
LICENSES, PERMITS, INSURANCE: All costs for required licenses, permits and insurance shall be borne by the Contractor.
Coastal Carolina University requires all contractual activities to be performed in a manner that is consistent with all applicable federal, state and local laws, regulations, rules, rulings and ordinances. These include, but are not limited to: the Occupational safety and Health Act, The Environmental Protection Act, The South Carolina Hazardous Waste Management Act.

IMPORTANT– Please Note - Contractors, we MUST have your Federal ID # (company) or Social Security # (individual) before processing any invoices for payment. Failure to provide this information will result in delay of payments until this information is received. Please include this information with your quote.



INFORMATION FOR OFFEROR’S TO SUBMIT
MINORITY PARTICIPATION (JAN 2006)
[bookmark: Text18][bookmark: Text19]Is the bidder a South Carolina Certified Minority Business?      Yes       NO
[bookmark: Text20][bookmark: Text21]Is the bidder a Minority Business certified by another governmental entity?       Yes       NO
[bookmark: Text62]If so, please list the certifying governmental entity:      
Will any of the work under this contract be performed by a SC certified Minority Business as a subcontractor?       Yes       NO
If so, what percentage of the total value of the contract will be performed by a SC certified Minority Business as a subcontractor?    Yes    NO
Will any of the work under this contract be performed by a minority business certified by another governmental entity as a subcontractor?       Yes       NO
If so, what percentage of the total value of the contract will be performed by a minority business certified by another governmental entity as a subcontractor?       Yes       NO
If a certified Minority Business is participating in this contract, please indicate all categories for which the Business is certified:
|_| Traditional minority
|_| Traditional minority, but female
|_| Women (Caucasian females)
|_| Hispanic minorities
|_| DOT referral (Traditional minority)
|_| DOT referral (Caucasian female)
|_| Temporary certification
|_| SBA 8 (a) certification referral
|_| Other minorities (Native American, Asian, etc.)
(If more than one minority contractor will be utilized in the performance of this contract, please provide the information above for each minority business.)
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