Background 
Africom is an Internet Access Provider with various point of presences  in Zimbabwe. We are embarking on a service availability improvement  project for all our point of service access points  power Sources  and power feeder and distribution Systems. The goal is to have our power available at least 99.7% per point of access through suitable solutions

Historical common cause of  power problems has been  commercial power load shedding , poor wiring ,  indefinite commercial power outages , reliance on power autonomy equipment with greater need for human intervention and  existing equipment ( batteries and generators )  reaching end of their manufacture defined useful life.

The proposed project calls for suitable suppliers to  submit proposal  outlining design , commercials , implementation plan , service levels  , vendor references , vendor supplier accreditation before 1 April 2014 to networkoperations@afri-com.net  and a hard copy delivered to the Procurement Officer at Tendeseka Offices Block 2 Harare.

Project Description 
The following solutions are expected:

- City Solution ( Harare CBD ) - The best option for city sites with at least 7days autonomy of working with no commercial power.

- Suburban Solution ( Within Harare ) - The best option for suburban sites with at least 14days autonomy with no commercial power.

- Out of Harare Solution - The best option for out of Harare sites with at least

- Mobile Solution to tow to any outdoor  sites in the event of a fault able to run for a full month with no human intervention.

Current  Components

Interested Vendors can request for a site survey 3days in advance during working hours to view one site to understand the setup by sending an email to networkoperations@afri-com.net 10 days before the due date for submissions.

Below is the listing of components currently setup on sites :

- Each Site has an AC Distribution box from either a shared site power or own ZESA Meter

- The commercial  mains supply is   +-220v Ac feeding into a DC rectifier inbuilt for supply into various components within the BTS

- The 220V AC load is 2Kv

- The  equipment uses DC -48v power supplier rectified through an inbuilt  transformer rectifier array(n+1 ).

- Within-in each cabinet there is a 150Ah Battery bank to assist in changeover to secondary mains sources.

- A few  sites have 12Kv  generators functional and some not fully functional however all the generators are close to end of life

- A few sites have a secondary leased 220V AC Source consisting of a  4.5KV Invertor + 420Ah Battery Pack + 280W 48V Solar feed into batteries with an 8 – 10 Hour Commercial Autonomy

- Most of our sites are power by Petrol 5kv generator if there is a power outage

Solution Requirements

- Each Solution Provider has flexibility of either choosing a 220V based solution or -48v solution

- The Proposed solution should be able to carry a rating of up to  4000VA

- Each site solution should be more than or equal to the stipulated autonomy period

- Each solution should have remote monitoring functionality for fuel level / batteries level , current source Commercial or Secondary

- All solutions are to  include weatherproof and security enclosures

- Each supplier to include a service level charge per quarter for maintenance of the solution

- Each Solution should be have at least a useful life of at least 48 months

Technical and Infrastructure Requirements 
The following systems can be proposed detailing the sizing of the systems and specifying the targeted site name :

- Solar system for both stand-alone and grid-tied systems as guided by site autonomy specification.

- Generator solution for both grid-tied and off-grid cases as guided by site autonomy specification.

- Hybrid Battery Generator System able to alternate between battery and gen power allowing generator  to recharge batteries when depleted as guided by site autonomy specification.

- Hybrid Solar – Generator able to only power generator when battery voltage is low due limited Sun Time.

Functional Requirements

- The power solution is to be cost-effective considering the location of site and the overall decision will be based on total cost of ownership over a 5 year period

- The system is to be efficient as well with minimal human interaction.

Estimated Project Duration

Each solution should have a relative project plan from effective from the day of contract signing.

Assumptions and Agreements

- Systems should   not be over dimensioned and over dimensioned proposals will not be considered.

- Systems should  not be  under dimensioned and under dimenisoned proposals will not be considered.

- After shortlisting is completed shall contractual terms be discussed for purposes of the proposal may all solutions be based on  a cash upfront basis.

For Additional Information or Clarification

For additional information or further clarifications please write an email to networkoperations@afri-com.net

Basis for  Proposal Shortlisting

Below factors will be used for shortlisting purposes

- Meeting Solution Requirements as guided by Project Description

- A solution with the most optimum total cost of ownership over a 5 year period

- Time to deliver equipment upon contract signing

- Proven Accreditation by any equipment manufacture with a solid track record in Africa

- Local Presence of a support team in Zimbabwe

List of Sites and location

- Fidelity Life Tower Harare

- Kadoma  NRZ Station

- NRZ Station Harare

- Ruwa NRZ Station

- Norton GMB

- Gweru FML Building

- Avondale 7 Arts

- Airport Harare

- TSL Harare

- ATHOL House Eastlea

- TSF Gleneagles Harare

- AGRICURA Southerton

- Sunridge Harare Drive

- Marondera NRZ Station

- Rusape  NRZ Station

- Chegutu GMB

- Kwekwe FML

- MT Pleasant Enda Zimbabwe

- Msasa Mukuvisi Woodlands

- Warren Park Harare Warren hills

- St Mary , Chitungwiza

- Nkulumane Bulawayo

- NRZ HQ Bulawayo

- Kenilworth Greystone Park

- Borrowdale Brooke

- Hilton Flats , Harare Avenues

- Causeway Post Office Harare

- Montrose , Bulawayo

- Killarney Heights , Avenues Harare

- Pockets Hill , Harare

- Beitbridge

- Fidelity , Mutare

- Stanley House , Harare CBD

- Mount Pleasant Bond

- Luveve, Bulawayo

- Zimra , Masvingo

- Victoria Falls

- Kariba Telone

- Gweru , NRZ Dabuka

- Greendale Water Tank , Harare

- Seke Unit D ,

- Dangamvura Mutar

- Kopje Harare