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State of Colorado

INVITATION FOR BID COVER SHEET
	

	Date:
	August 22, 2008
	IFB Number:
	IFB-09-AEA-118-JW

	Return all Sealed Bids to:
	Department of Personnel & Administration

633 17h Street., Suite 1600
Denver, CO 80202
	Purchasing Agent:
	John P. Weber, C.P.M., CPPB

	IFB Opening Date:     
	September 30, 2008
	IFB Opening Time:
	3:00p.m. (MST)

	Water Treatment Chemicals and Related Services.,

Heating and Cooling Systems for State Owned Building
All Bids Shall be Quoted F.O.B. Destination unless Otherwise Specified

Per the attached specifications, terms and conditions


	F.E.I.N.:
	
	Payment Terms:

 (Minimum of Net 45)
	

	Delivery Date:
	
	
	

	Authorized Signature:
	

	Typed/Printed Name:
	

	Title:
	

	Company Name:
	

	Address:
	

	City:
	
	State:
	
	Zip:
	

	Phone Number:
	
	Fax Number:
	

	Contact for Clarifications:
	

	Title:
	

	Phone Number:
	
	Fax Number:
	

	E-mail Address:
	

	The purpose of the coversheet is to fully identify respondents so they may be considered, to quickly identify the costs and billing terms, and other basic information. Submit this coversheet (completed and signed), price page(s), supporting descriptive/technical literature for substitutes where applicable, and other enclosures requested or relevant to this solicitation. In the interest of minimizing processing time and economizing our resources, unrelated or unsolicited material submitted with offers will not be considered or retained on file.   Vendors are to complete the presented format.  Also, in submitting this coversheet, you are verifying receipt of the original BIDS notice and file attachments.  Where modifications are issued, you need to additionally acknowledge receipt of the number of modifications above where indicated. 


	IMPORTANT: The following information must be on the outside of the Bid Return Envelope: 

Bid Number -Opening Date and Time

Please be advised that telegraphic or electronic bids (Fax, Western Union, Telex, e-mail, etc.) cannot be accepted directly in the Purchasing Office as a sealed bid.  Bidders are urged to read the solicitation document thoroughly before submitting a bid.  Bidders are required to submit Federal employer Identification Number (F.E.I.N.) prior to payment from the State of Colorado.

The State respects the environment and desires to do business with vendors who share this concern.  Accordingly, the vendor who is awarded this solicitation agrees that, wherever required, all reports, catalogs, correspondence, or other submittals will be made on recycled paper and with copying on both sides of the pages.  (Recycled paper meaning not less than 50% of the total weight consisting of secondary and post-consumer waste, and not less than 10% total weight consisting of post-consumer waste.) 

In accordance with Procurement Code, CRS 24-103-207.5 titled -Purchasing Preference for Environmentally Preferable Products; bidders responding to this solicitation may seek to qualify for the preference and governmental bodies conducting this solicitation shall award a contract to a bidder who offers environmentally preferable products subject to the conditions in the Code and Procurement Rules.”   

Low Tie Bids: Low tie bids shall be decided in accordance with the provision of C.R.S., Section 24-103-202.5, as it currently exists or is hereafter amended, which give a preference to resident bidders.  Any bidder who wishes to be considered a "resident bidder" for purposes of the tie bid procedure provided in C.R.S., Section 24-103-202.5 shall include with their bid proof that he/she meets the definition of resident bidder as set forth in either C.R.S., Section 24-103-101(6)(a) or C.R.S., Section 24-103-101(6)(b).


1.0  General

Awards

The State reserves the right to make, solely at its discretion, partial and/or multiple awards. The State intends to award one Contract to a single vendor capable of fulfilling the anticipated volume needs for Water Treatment Chemicals and Related Services.
Contract Attachment

The attached Contract (Exhibit A) represents sample language used in State of Colorado Contracts for services.  All State contracts will comply with the provisions outlined in authoritative guidance provided by the State Controller's Office.  SPECIAL PROVISIONS also are in integral part of the contract.  Failure of a Bidder/Respondent to accept State of Colorado contract terms and conditions may serve as cause for disqualification of an offer.

Contractual Obligations
This solicitation including documents linked and attached, the vendor's offer and all documents, modifications, and agreement terms and conditions will form the contract between the parties.  Any additional terms and conditions proposed by the vendor must be submitted with their offer in order to be considered.  The terms and conditions on any offeror(s) time sheets, invoices, or other forms, including but not limited to indemnification, limitation of liability, or cancellation fees, shall be void and of no effect against the State of Colorado or any of its employees.  The offeror(s) and State’s rights and obligations shall be solely governed by the terms and conditions of the price agreement.  Any employee’s signature on offeror(s) forms shall be effective only to establish receipt of services.

Demonstrated Performance Ability, Reference Requirements and Site Visits

Bidder must be able to demonstrate the ability to perform the requested services.  Bidders must have a minimum of ten (10) years experience, a minimum of (1) Chemical Engineer on staff and must submit a minimum of three (3) references.  One (1) reference must be where commercial services of similar size, scope and complexity were performed and two (2) additional references which do not need to be of similar size and scope. All references must be able to substantiate the vendor's primary business is the same as that requested herein.  It is the responsibility of the bidder to ensure the information provided is accurate and current. The State reserves the right to conduct an on-site inspection of the contractor’s facilities as it relates to the service being requested at any reasonable time and may require additional information of the apparent successful bidder/offeror to determine their ability to perform.  For each reference submitted, bidder must provide the following information:

1)
the name and address of the company

2)
current contact name, telephone number or other number where the contact can be reached  

3)
period of service: mm/yy/ to mm/yy .  

4)
the location of where services were/are being performed

5)
a brief description of the services

Work Plan

Provide a written plan to include a back-up plan which details the process that will be used to assure services will be provided in accordance with the specifications herein to the State’s satisfaction. The vendor’s plan must describe how and with what manpower and equipment the vendor will accomplish the requirements of the State. All work shall comply with federal, state, and local codes. In no case shall a product be used in a manner inconsistent with its labeling
Personnel employed by the Contractor in this work will be duly trained, competent and appropriately licensed, if applicable.  Contractor’s employees are to be clearly identified by appropriate uniform or other markings on their person that would identify them while they are authorized to be on State property while performing their tasks. Personnel assigned to the State sites must pass a background check. At any time State Patrol may question Personnel at any Capitol Complex Facilities, resulting in an arrest if warrants are issued.
Electronic Copy
Bidder/offerors are requested, but not required, to provide an additional electronic copy of their response including necessary brochures, catalogs, attachments, and other items on a disk or CD in a universally accepted format such as Adobe .pdf or Microsoft Office in addition to the required hard copy to facilitate evaluation and processing.  Proprietary/confidential information must be submitted on a separate disk and be clearly marked as such.  Documents should be single sided on recycled paper, and easy to copy/scan (no bound material, minimize use of tabs and clips, etc).  Paper should be white or extremely light paper and no dark backgrounds.  Enhance images for pages with a poor image quality.  The original hard copy in all cases is the official record.
Estimated Quantities
The volumes stated in this solicitation are estimates only and the State makes no guarantee of actual volume or purchases as a result of a contract. See Exhibit B for combined estimated annual usage and usage by location.
Insurance
The awarded vendor will be required to submit a certificate(s) showing insurance coverage as outlined in the linked State of Colorado Solicitation Instructions/Terms and Conditions

Modifications

All modifications shall be in writing and posted to BIDS.  Vendors are responsible for checking BIDS prior to the opening date and time for solicitation modifications.

Performance
Awarded offeror(s) are expected to become familiar with current Capitol Complex’s rules, regulations and policy’s regarding the use and handling of chemicals, as well as comply with any Executive Orders or other decisions regarding the State of Colorado in regards to the performance of the contract. 

Public Opening of Bids 
Only the names of Offerors submitting bids will be read at the bid opening.  

2.
Bidder Response Format

Submit an original plus three copies of the sealed bid properly marked.  

Bidders must comply with and or submit the following item(s) in order and clearly labeled: 

a. Signed cover sheet.

b.  Provide three satisfactory references per the above requirements outlined under Demonstrated Performance Ability, Reference Requirements and Site Visits
c.  Completed Pricing Sheet

d.  Brief Work Plan

e. Vendor Disclosure Statement (only if it applies)
3.
Mandatory Pre-Bid Walk-through Site Visit:

A Mandatory Pre-Bid Walk-through Site visit for all potential Bidders will be held:

September 4th and 5th
(September 5th walk through date will be required if all sites visits were not completed on September 4th)
9:00 AM to approximately 4:00 PM each day or until all sites have been visited 

Starting at 1525 Sherman St. B-15, Denver, CO.
NOTE* If the second day (9/5) is required to complete the Mandatory Walk through Site Visit, the starting point will be the same as the first day (1525 Sherman St. B-15, Denver, CO.) Only those bidders that attended the September 4th Walk through and Site Visit 
This is a MANDATORY Pre Bid Walk through and Site Visit. All prospective bidders will be required to complete a sign in sheet for September 4th and September 5th (if required). Bids submitted by Contractors who did not complete the sign in sheet FOR BOTH DAYS, will not be considered. Bidders will not be allowed to revisit any sites after the mandatory Walk though and Site Visit dates above.
Bidders shall provide their own transportation and parking for the visit to each site.  Most of the sites are in a 4-block radius of 1525 Sherman; however, Bidders will be expected to also drive to and attend the walk-troughs’ at the Lakewood area locations.  At each site, a reasonable amount of time will be told to the Group to allow time to arrive at the next site.   

Please note, questions will not be taken or answered during the walkthrough.  Contractors may submit questions as a result of the walk-through and the review of the specifications for this solicitation by submitting in writing (email preferred with WORD attachment) to the Point of Contract listed on page one of the BIDS solicitation notice.  Questions are to be submitted no later than:  September 10, 2008, 3 PM, MST.  

A compilation of questions and answers will be formally posted on the Colorado BIDS for Bidder review no less then 7 calendar days prior to the bid closing to allow prospective bidders time to complete and submit their bids.  Undocumented questions and answers will not be considered in the evaluation process.

4.
Program Background

The State of Colorado, Dept. of Personnel and Administration (DPA) is responsible for the State-owned buildings.  The Division of Central Services (CS) in their Capitol Complex Services Program is tasked with providing environmental systems for those State buildings.  The heating and cooling systems in the State-owned buildings vary between sites and include chilled water, steam, and hot water systems; and are run as open and closed loop systems.   The systems also have varying ages of use and various levels of condition that requires constant monitoring and frequent maintenance.  

Site locations For Chilled Water Systems

The seven (7) Capitol Complex buildings located in the Denver, CO metro area have varied water systems consisting of open and closed loop systems.  Each site has a unique system that requires system maintenance.

1)
1341 Sherman - Power Plant Building:  system is a chilled water, closed loop system with Glycol that consists of a 900-ton chiller, a 650-ton Absorber, and 2 water side economizers. The open loop system consists of 1 air coil tower and 1 tower with 3 points of chemical feeds.
2)
201 East Colfax - State Office Building:  system consists of a 650-ton chiller which feeds into the main closed chilled water loop. 

3)
1525 Sherman - State Services Building:  system is an open loop system for the Baltimore air coil tower that has 1 point of chemical feed. 

4)
1570 Grant:  System has two (2) 200-ton chillers and each has a water side economizer.  The open loop system consists of a cooling tower with an indoor sump and has 2 points of feed for chemicals.

5)
1881 Pierce (Lakewood, CO) location system has two (2) 270-ton chillers and 1 water side economizer.  The open loop system consists of 2 cooling towers and has 2 points of feed for chemicals.

6)
The Capitol’s (200 East Colfax) system has a 150-ton chiller and a water side economizer.  The open loop system consists of 1 cooling tower and has 2 points of feed for chemicals. 

7)
690 Kipling (Lakewood, CO) system has three (3) 300-ton chillers and 1 water side economizer.   The open loop system consists of 2 cooling towers and has 2 point of feed for chemicals.  This is the only building that is normally scheduled for 24/7 operations.

Site Locations for the Steam Treatment Systems (in Denver, CO):

1)
The point of feed for steam is at 201 East Colfax - State Office Building and 1575 Sherman Street - Human Services Building.  A steam boiler is located at 1570 Grant (Denver, CO).

Site Locations for the Hot Water Closed Loop Systems (in Denver, CO):

1)
Systems are located at 1313 Sherman - Centennial Building, 200 East 14th Street-  Legislative Service Building, 201 East Colfax - State Office Building, 1525 Sherman -  State Services Building, 1575 Sherman - Human Services Building, 1881 Pierce, and 400 East 8th Avenue - Executive Residence. 

System Expansion:
There is a possibility of water system expansion, improvements, or other changes as is required by need and funding availability.  Those improvements and expansions would result in additional water treatment services needs and would be cost effective to become an addition to the services provided by the then current Contractor.  It would be also prudent to stay with the then-current Contractor instead of hiring out a small piece of a large water treatment service and plan that may have detrimental impact if the two services and/or future equipment were incompatible.  For the purpose of this bid proposal, this topic of system expansion is for only informational purposes.   

5.
Purpose of this Solicitation and Resulting Contract
The Department of Personnel and Administration Procurements and Contracts Unit seeks bids for providing delivery, handling and distribution, of all water treatment chemicals. The awarded Contractor shall also maintain appropriate levels of chemical in all existing open loop, close loop and steam systems at each of the sites listed above. The chemical treatment shall ensure no biological growth and scaling occurs in any of the systems.  The awarded Contractor shall fulfill all specifications below and keep the systems operational. Included in the cost of all chemicals used shall be all testing, analyzing, site visits, reports, site inspections, all services listed throughout this statement of work document. The offeror(s) whose response is determined to be most advantageous to the State of Colorado will be awarded a State Contract for one year, with the option to renew for nine (9) additional one year periods.
NOTE* Option to renew for up to nine (9) additional years is pending upon approval for the State Purchasing Office. If approval is not granted, the maximum renewal period shall be no more then four (4) additional one year terms for a maximum of five (5) years. 
Orders will be placed by the State on an "as-needed" basis. Capitol Complex must maximize all resources available to support its operations.  In the event that the awarded Contractor can not meet the delivery requirements at time of order, the State reserves the right to obtain required chemicals and/or water analysis from alternative sources. Any cost difference from the chemicals ordered from the alternate source and the price of the awarded contract, shall be charged back to the awarded contractor.

6.
Pricing and Term Information

Bidders shall submit pricing for required services and chemicals as listed in pricing section. If there is a cost associated with the transition to new systems, the Bidder shall submit all costs associated with the new equipment including, but not limited to; equipment, installation, transportation and labor in the pricing section. 
Prices shall remain firm through the first year of the contract from the date of Contract approval by the State Controller. The Contractor may seek a price adjustment, in any succeeding period, by submitting detailed written justification to the State which substantiates any price adjustment request.  Only one such adjustment will be allowed in any twelve-month period of this Contract.  Any request for an adjustment must be submitted to the State at least 90 days prior to the current contract’s expiration date. In the event the negotiations do not result in any agreement between both parties, this contract may be canceled and may be rebid with no penalty to the State.

7.
SCOPE OF CHEMICAL WORK  

The Contractor shall provide delivery, handling and distribution, of all water treatment chemicals. Contractor shall also maintain appropriate levels of chemical in all existing open loop, close loop and steam systems at each of the sites listed above. The chemical treatment shall ensure no biological growth and scaling occurs in any of the systems.  The Contractor shall fulfill all specifications below and keep the systems operational. Included in the cost of all chemicals used shall be all testing, analyzing, site visits, reports, site inspections, all services listed throughout this statement of work document.. 
7.1.

EQUIPMENT: All equipment provided shall remain the property of the contractor. The State shall not incur any contractor associated costs for the equipment. Contractor shall be responsible of all repair and replacement costs for all contractor owned equipment for the life of the awarded contract.
Contractor shall provide chemical feed containers at each DPA facility water treatment site.  Refer to Section 7.9, Chemical Storage Requirements. Cost to install any equipment shall be included in the bid under Transition Pricing. See Section 18 Pricing for details. 

The Contractor shall provide chemical controllers at each DPA facility water treatment site.  The Contractor shall provide all chemical controllers. The controllers for cooling tower system must control corrosion and scale inhibitor in real time, on active chemistry rather then total chemical concentration. Additionally, the controllers must control duel biocide addition via timers as well as the conductivity.  The controllers must be accessible via a contractor provided website that is password protected. All information collected and stored in the controller must be viewable on-line from any computer for DPA’S view.  The controller unit must also have an automated system that enables it to notify anyone designated for alarms via e-mail, pager or cell phone; and includes the Contractors staff and the State Mechanical Shop Supervisor or their delegate.  The controllers must be able to automatically test and control corrosion inhibitor; without the need to perform these tasks manually. These electronic controllers must be capable of acquiring at least 3 leed certification points. 

Required System Capabilities: 

· Capable of controlling within +/- 5 ppm the total scale and corrosion inhibitor in the recirculation water without using molybdenum-traced products.

· Graphically reporting the chemical dosage in the cooling water systems.

· Capable of compensating for un-metered make-up and/or blow down.

· Capable of controlling chemical levels regardless of the number and/or control of the cycles of concentration.
Contractor is responsible to insure that the equipment provided is fully operational for its intended use. In the event of contractor owned equipment failure, contractor shall be responsible for immediate clean up if applicable and shall replace or repair the defective equipment and restore system to full operation within 5 business days after notification from the State Mechanical Shop Supervisor or their delegate. The State shall not be responsible for any costs incurred by the contractor for the repair, clean up, or replacement of the defective equipment.
7.2.

GOVERNMENT REGULATIONS

All chemicals proposed by the Bidder for use at DPA facilities shall be verified by the Bidder as acceptable for use in the State of Colorado. All chemical containers delivered to any State Building shall have on the outside of the container easily visible documentation stating the compliance with, United States Department of Agriculture (USDA), United States Food and Drug Administration (FDA), United States Department of Environmental Protection Agency (EPA), and the United States Department of Transportation (USDOT) requirements to include application, packaging, and labeling the chemicals. Contractor shall also provide and electronic copy to the State Mechanical Shop Supervisor of all the above documentation prior to any chemical delivery to any State building.

Prior to chemical introduction, the Contractor shall provide an electronic copy of all documentation to the State Mechanical Shop Supervisor all standards of the local municipality, the State of Colorado, and  Federal regulations have been met for all discharges (fluid or solid matter) into the sewerage system from cooling tower bleed-off, boiler blow down, or system draining,

7.3.

MATERIAL COMPATIBILITY

Prior to chemical introduction, the Contractor shall ensure and provide an electronic copy of documentation to the Mechanical Shop Supervisor that the chemicals used in the existing water treatment systems shall have no detrimental effect on the metallic or non‑metallic materials in the equipment being treated when used in accordance with Contractor's instructions.  The Contractor is responsible to follow all manufacturers’ recommendations.

The Contractor shall be responsible for any damage to any and all water system piping and equipment as a result of their chemicals being introduced into the existing systems.  Contractor shall be responsible to schedule equipment inspection with the State Mechanical Shop Supervisor or their delegate prior to introducing any chemicals into any system to verify and document equipment condition. Contractor shall also be responsible to schedule with the State Mechanical Shop Supervisor an additional equipment inspection at the end of each treatment season (heating or cooling) or as requested by the State Mechanical Shop Supervisor to analyze the performance of the chemical treatment to ensure equipment condition has not deteriorated.  Contractor shall be responsible to perform any additional work to ensure no damage will result in any of DPA’S water treatment systems in the mixing of the existing chemical treatment and the chemical treatment the Contractor provides. This additional work may include put is not limited to total system flushing, glycol replacement, chemical feed lines and Check valves at points of feed etc.   

7.4.
SERVICE LEVEL AND RESPONSE TIME

The Contractor shall visit each water system site a minimum of once a week to verify proper operation of Contractor supplied equipment, take water sample to determine proper chemical levels and make any needed adjustments.  Contractor shall provide a standard services report to the Mechanical Shop Supervisor via e-mail within 24 hours of the site visit.

7.5. WRITTEN SERVICE REPORTS
Contractor shall provide a monthly written report by the 5th of each month to the State Mechanical Shop Supervisor on a form supplied by the Contractor and approved by State Mechanical Shop Supervisor or their delegate for this purpose.   The report shall, at a minimum, include the following essential data:
a. Calcium hardness

b. M-Alkalinity

c. Chlorides

d. TDS/M-OHMS

e. All chemicals levels

f. Fluorescent dye content

g. pH levels

h. Conductivity

i. Nitrite

j. List recommended parameters for all listed tests (A through I ).
k. The written report shall state all unusual or undesirable conditions along with the correct remedy.  

The Contractor shall provide three (3) field chemical test kits for the water systems to DPA within 1 week of the start of the contracted services.  The Contractor shall provide three (3) eight-hour training sessions for up to three (3) DPA/Central Services employees on how to use the chemical test kits for the chemicals being used by the Contractor for each of the water systems and the equipment provided by the Contractor (ie. tanks and controllers) for each site.  The training timing shall be determined by DPA.

The Contractor shall be available to DPA 24 hours a day and 7 days a week (“24/7”).  The Contractor’s response time shall be to arrive at the DPA site within four (4) hours after being notified by phone by a designated DPA staff member.  Under emergency circumstances, the Contractor shall arrive at a DPA facility within one (1) hour after being notified by phone by a designated DPA staff member.  

At least two (2) qualified backup Contractor employees, who are familiar with all sites, shall also be available.  The Contractor shall be available for calls on specific problems should they occur.  The Contractor shall provide to DPA a current phone number and an alternative 24/7 emergency contact phone number.  

7.6.
CHEMICAL STORAGE, DELIVERY, ANALYSIS, AND HANDLING REQUIREMENTS

The Contractor shall not have chemical storage, drum handling, or chemical disposal at DPA’s sites.  All product deliveries must be made to the point of feed for each facility.  Only stainless steel feed tanks will be used.  Plastic and mild steel containers of any size are not acceptable.  Powdered products are not to be used unless specifically approved in writing prior to installation by a designated DPA staff member.  To eliminate chemical handling by DPA’s site personnel, all products must be capable of being fed neat (without dilution or contact) into the open and/or closed loop systems from Contractor-supplied on-site feeder containers.  In order to minimize liability, DPA requires the Contractor to follow the chemical delivery and storage requirements below:
All orders for chemicals shall be delivered within 15 days after order. Contractor shall contact the State Mechanical Shop Supervisor or their delegate to set up delivery time to assure that State personnel are available at time of delivery.
7.7. 
TUBE INSPECTIONS
The Contractor shall have a representative present when the chiller condenser heads are removed by State personnel for tube inspection at least once (1) per year or as requested by the State Mechanical Shop Supervisor. 

7.8. WARRANTY
The Contractor shall warrant that all chemicals furnished and used in any of the systems will prevent the adherence of scale on the interior of the condenser tubes and shall minimize the adherence of scale to all other parts of any of the systems without causing excessive corrosion on any part of the system.

7.9. CHEMICAL STORAGE REQUIREMENTS
a) Storage container type must be approved by the Environmental Health and Sciences (EH&S).  The container must have an appropriate lining if storing corrosive chemical material.  

b) Contractor is responsible for installation and maintenance of chemical storage containers at each facility site.   
c) Secondary containment volume must be at least 150% of the delivered chemical storage container volume.

d) Storage containers must have bottom drain capabilities to ensure positive, flooded suction for chemical pumping and injection and to allow complete emptying of the vessel.

e) The Contractor shall retain ownership of storage containers.
f) The storage containers must be vented and fitted with appropriate fume suppression equipment during delivery.

g) The Contractor accepts legal liability for delivery of all products and storage containers.  
h) If a storage container or the chemical delivery equipment leaks or spills, the Contractor shall be responsible for the cost associated with clean up, removal of spilled chemical and replacement of storage container.

7.10. CHEMICAL DELIVERY REQUIREMENTS
a) The Contractor’s chemical transport equipment must comply with USDOT requirements for transporting hazardous material.

b) The Contractor shall not store any empty or full chemical transport equipment on site at DPA facilities.

c) The Contractor shall ensure deliveries are made by their employees who are chemical handlers and who are:

i) Certified in HAZMAT compliance.

ii) Equipped with Personal Protection Equipment (PPE) on-site for delivery and transfer of chemical.  
iii) Equipped with items required to handle spills and any unexpected incidents.
d)
All orders for chemicals shall be delivered within 15 days after order. Contractor shall contact the State Mechanical Shop Supervisor or their delegate to set up delivery time to assure that State personnel are available at time of delivery.
8.0.
TRANSPORTATION REQUIREMENTS

The price must be calculated as freight on board (FOB) at destination, freight prepaid. The Contractor’s price proposal shall include all charges for transportation, packaging, pallets, containers, etc., necessary to complete all deliveries. 

9.0
TROUBLESHOOTING CAPABILITIES AND ANALYTICAL LABORATORY SUPPORT
The Contractor must have laboratory facilities capable of performing a wide array of analytical work to facilitate monitoring, control, and troubleshooting of all DPA sites chemical water treatment systems.  The Contractor shall provide all laboratory services.  In the event these services are subcontracted or the use of independent laboratories is needed, the Contractor must first obtain writing authorization and approval by State Mechanical Shop Supervisor or their delegate for a one-event use.  Laboratory services include: corrosion coupon analysis, water analysis, deposit analysis, microbiological analysis, ion exchange resin analysis, analex cartridge analysis, fuel oil analysis, RO membrane analysis, and metallurgical analysis. Contractor shall provide an electronic copy of all laboratory test results as requested by the State Mechanical Shop Supervisor and the Contractor must provide the information within 5 business days of the request.
10.
EVAPORATIVE CONDENSER WATER TREATMENT SPECIFICATIONS
1) Chemicals:  Contractor shall provide chemicals at levels necessary to treat the cooling tower/condenser water system for scale, corrosion, microbiological growth, and fouling.  Chemicals must be compatible with existing treatment program. All open, re-circulating water chemistry must be controlled by active rather then total chemical concentration. 

a) Scale and corrosion Inhibitor(s):  Contractor shall provide chemical treatment at levels in a liquid non-chromate, non-molybdenum, non-polluting program that is capable of copper corrosion inhibition.   Molybdenum/molybdate is not prohibited for use.

b)  Biocides:  Contractor to provide biocides used to prevent algae and microbiological growth in the tower and the condenser system.  Provided at levels to maintain a total aerobic microorganism level below 10,000 cfu/ml.  Biocide addition must be based on bacteria counts rather then ORP. 
c) Oxidizing:  Contractor to provide chemicals at levels of bromine formulation that maintains the halogen level in accordance with CTI standards for Legionella risk control dated February 2000 (see APPA website for more information www.appa.org/) and meets the following criteria (a) 0.5-1.0 ppm frees halogen for non-stabilized halogens in liquid and dry form and (b)  0.5-1.5 ppm total halogen residuals for stabilized products.

11.
MATERIAL SAFETY DATA SHEETS (MSDS)
In order to have quick access to all technical and safety information regarding the water treatment program, the Contractor shall provide an Administration Notebook for each facility’s water treatment system.  The notebook of information shall be on 8-1/2” x 11” pages and all pages shall be legible at no less than 10 font size text.  For each site’s chemical treatment, at the very least, this notebook shall contain clearly labeled sections for the outline of the chemical program; identify the chemicals used in the system dates when chemical storage containers were filled and with what chemical; all chemical control test procedures; and Log Sheets of chemical testing results; product bulletins; material safety data sheets (MSDS) for all of the chemicals in use in the system; feed and control equipment specifications; and Service Reports for every site visit. 

The Contractor shall include MSDS sheets of all chemicals and products used including bulletins/fact sheets. MSDS sheets shall be located at each site’s point of feed. Contractor shall also provide to the DPA representative a 3 ring binder containing all MSDS sheets on all chemicals and products used in all sites. Before Contract start date, awarded Contractor shall submit to the State representative for approval a list of each item of supply or material to be used.  The Contractor must supply all MSDS sheets with their bid for all supplies proposed. 

12.
PROGRAM ADMINISTRATION

The Contractor shall assign a “single point of contact” to the State Mechanical Shop Supervisor and supply all contact information that can provide information for operations issues, accounting issues, and contract issues.  This person can be the same as the Contractor’s on-site representative for the weekly site visits if the person assigned has the ability to handle the relative questions.  

13.
ANNUAL BUSINESS REVIEW

The Contractor must present to the State Mechanical Shop Supervisor a yearly business review electronically 30 days prior to the end of each Contract term. This review shall include the treatment program that addresses all treatment programs, their effectiveness, and future objectives. The Contractor shall meet at these times with the State Mechanical Shop Supervisor or their designated DPA staff to discuss all treatment programs, their effectiveness, and future objectives.
14.
SUBCONTRACTORS
No subcontractors are to be used in any portion of your services unless approved in writing by the State Mechanical Shop Supervisor with copy submitted to State Contracts Administrator. 

15.
ENVIRONMENTAL PREFERRED PRODUCTS (if available)
The Contractor shall submit information; including any reference to a nationally recognized third party certification entity that has certified the product or service as Environmental Preferable (i.e. Green Seal, EPA, Scientific Certification Systems, etc.). If costs are comparable, preference shall be given to the Contractor that provides Environmentally Preferable Products.

“Environmentally Preferable Products” means products or services that have a lesser or reduced adverse effect on human health and the environment when compared with competing products or services that serve the same purpose.

16.
TRANSITION PLAN
Bidder’s shall submit with their bid a transition plan that addresses the requirements below.

1)
Cooling System transition shall start no sooner than November 1st 2008 and shall be fully completed on or before March 1st 2009 for all cooling system locations
2)
Heating system transition shall start no sooner than June 1 2009 and shall be fully completed on or before September 1st 2009 for all heating system locations.

3)
Work with current vendor (Nalco Chemical) to expedite transition and change out of tanks

4)
All coordination of any transition schedules shall be through the Mechanical Shop Supervisor or their delegate. 

5)
Vender shall supply any and all equipment needed to complete the transition. The state will not supply any tools or equipment to venders for any use.  
17.
AWARD EVALUATION

The State shall take the lump sum transition cost for all locations as one sub-total (A). The State shall add the monthly service charge for each location together and multiply by twelve (annual charge) for another sub-total (B). The state shall then add the costs for the estimated annual chemical usage for all locations as another sub-total (C). The State will add all sub-totals together (A+B+C) to arrive a total cost for award consideration.
18.
PRICING SHEETS
A)
TRANSITION COST: Lump sum pricing to install all required equipment, for all locations, necessary to perform the services as required in Invitation to Bid IFB-09-AEA-118-JW. All equipment installed shall remain the property of the contractor. The State shall not purchase nor assume ownership or responsibility of any installed equipment.




Lump sum Transition cost for new equipment $________________

B)
MONTHLY SERVICE CHARGES: Monthly service charge price for each location shall include all service calls, site visits, adjustments, monitoring and reports as per the specifications and requirements listed in the Invitation to Bid for each location.

NOTE* There are multiple systems located at several of the locations listed below. Bidders may submit one monthly service charge for a location to cover all systems at that location. If a single service charge is listed to cover all systems at a single locations bidders must state which additional locations are included.

Example:
Chilled Water System

Item 3)

1525 Sherman – State Services Building


Monthly Charge $45.00
Hot Water Closed Loop System
Item 14)
1525 Sherman – State Services Building


Monthly Charge $Included with Item 3
Chilled Water Systems (Open and Closed Loop Systems)
Item 1)
1341 Sherman - Power Plant Building

Monthly charge
$_____________
Item 2)
201 East Colfax - State Office Building:

Monthly charge
$_____________

Item 3)
1525 Sherman - State Services Building:

Monthly charge
$_____________

Item 4)
1570 Grant:




Monthly charge
$_____________
Item 5)
1881 Pierce (Lakewood, CO):


Monthly charge
$_____________
Item 6)
The Capitol’s (200 East Colfax):


Monthly charge
$_____________
Item 7)
690 Kipling (Lakewood, CO):


Monthly charge
$_____________
Steam Treatment Systems

Item 8)
201 East Colfax – State Office Building

Monthly Charge
$_____________
Item 9)
1575 Sherman – Human Service Building
Monthly Charge
$_____________
Item 10)
1570 Grant – Steam Boiler

Monthly Charge
$_____________
Hot Water Closed Loop Systems
Item 11)
1313 Sherman – Centennial Building

Monthly Charge
$_____________
Item 12)
200 East 14th Street – Legislative Services Bldg.
Monthly Charge
$_____________

Item 13)
201 East Colfax – State Office Building

Monthly Charge
$_____________

Item 14)
1525 Sherman –State Services Building

Monthly Charge
$_____________

Item 15)
1575 Sherman – Human Services Building
Monthly Charge
$_____________

Item 16)
1881 Pierce (Lakewood, CO)


Monthly Charge
$_____________

Item 17)
400 East 8th Ave. – Executive Residence

Monthly Charge
$_____________
C)
CHEMICAL USAGE: The chemicals listed below are Nalco Chemical product numbers currently in use and are for reference only. See Exhibit B for estimated annual usage by location. All chemicals bid must be equal to those listed below.  Please reference Exhibit C of the solicitation for the corresponding Material Safety Data Sheets. Note all pricing must be priced per pound, no exceptions. If your product is normally priced per gallon, you are required to convert the pricing to cost per pound.
1)
23265


950 lbs.


COST PER POUND

$___________
2)
2838


345 lbs.


COST PER POUND

$___________

3)
ST20


1610 lbs.


COST PER POUND

$___________

4)
C-4710


740 lbs.


COST PER POUND

$___________

5)
22352


76 lbs.



COST PER POUND

$___________

6)
1820


800 lbs.


COST PER POUND

$___________
7)
2593


745 lbs.


COST PER POUND

$___________
8)
Solid Bionox

20 lbs.



COST PER POUND

$___________
9)
3DT265


300 lbs.


COST PER POUND

$___________
10)
Nalclean 8910

2800 lbs.


COST PER POUND

$___________
11)
Trac 102

80 Gallons


COST PER POUND

$___________
The following products are test reagents and are used in very small quantities during the year. These items are normally supplied in two (2) ounce bottles or gram sized “pillows”. The cost of these items will not be used in the award evaluation however all bidders are required to provide a cost for these items. Specify the cost and package sizes available for each.

12)
460-S0771 Soln N-2 Titrant, form liquid
Unit size___________
Cost per Unit
$___________
13)
460-S0770 Soln N-1 Indicator. Form liquid
Unit size___________
Cost per Unit
$___________
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